## Sheet1
PROJECT : NEW HOSTEL TOWER (4 BLOCKS) & CAFETERIA AT BIRLA INSTITUTE OF TECHNOLOGY, MESRA, RANCHI
BILL OF QUANTITIES
Item No. | Description of work | Unit | Quantity | Rate (Rs.) | Amount (Rs.)
(I) | STRUCTURE WORKS
Note: The BOQ should read in-conjunction with specification, drawing & structural notes. The cost shall include the cost of the material, transportation, taxes, duties, lifting, shifting, storing, handling, installation, till handover. Boq not includes external development works, External Staircases, etc.
1 | EXCAVATION:
General Notes: a) Contractor shall visit the site and get acquantained with site conditions, nature of soil, water likely to get collected by runoff or rain and logistics. b) Contractor shall take all required permissions from the appropriate Authorities for excavation, blasting, carting away materials etc as applicable. c) Contractor shall, based on his information in (a) above plan appropriate dewatering system as deemed fit for the nature of soil, and other precautionary measures during the excavation and construction. The contractor shall submit the method statement for dewatering to the Engineer for approval. Cost to include dewatering system with respect to inclined weather, at all levels for all activity. d) Dewatered water/ slush shall be drained out by suitable means through authorised water outlets, including obtaining the permissions of Authorities.
e) Contractor shall take all necessary steps to ensure that the slopes of the excavated pit are safe at all times.The Contractor shall design appropriate slope protection system and shall obtain Engineer's approval, and shall take all precautions not to damage or disturb the retention system. In case any damages occur for any reasons what-so-ever the Contractor shall make good such damages at his own risk & cost. f) Contractor shall keep final founding strata absolutely clean by removing loose, slushy soil, murrum and weathered rocks with necessary tools & tackles, cleaning the surface by wire brush and carting away the debris, dewatering to keep site dry at all times till laying and curing of PCC, footing, foundation etc complete. g) Contractor shall level the final founding strata / excess excavation with plum concrete or PCC at the Contractor's cost.
h) Contractor shall do necessary shoring, strutting with approved timber/steel accessories wherever necessary, as approved by the Engineer. i) Contractor shall take the contour levels jointly with the Engineer and shall obtain prior written approval before starting any excavation/ filling at every 3 / 5 m grids for arriving at the actual quantity as described by the Engineer. He shall submit jointly signed " Original Ground Level (OGL) " records to the Engineer. j) Measurement for Excavation carried out by manual / mechanical appliances using various attachments such as bucket or rock breaker or chisel shall be done based on the plan area of the PCC. Payments shall be made on the volume of earth computed with PCC plan area and levels taken before and after excavation in the area. Any slope / shotcreting / guniting required by the contractor shall not be paid extra. k) Contractor shall make sure that his vehicles / plant / machinery do not make the roads dirty by making appropriate arrangement for washing / cleaning of the wheels.
l) The rate shall include all necessary setting out of building, excavation line, barrication by grid/plot marking, survey by Total station, transfer of bench mark, etc., complete
m) The quoted rates includes segregating of good quality excavated earth from the clay / silty soil and storing in designated area for further treatment within the site premises for future landscape purposes including preserving top 300 mm layer of existing soil to meet MOEF requirements. No extra is payable towards double handling.
n) Constructing of temporary roads, temporary drains, rerouting of existing roads, etc. complete. Rate shall include required materials, labours, machineries to complete the works all as per engineers instruction.
o) Necessary safety barrication required during the execution of works shall be done by the contractor as per the drawing issued.
1.1 | Excavation: General excavation by mechanical means in all types of poclainable soil including dense soil, filled up earth, disintegrated / weathered / soft rock. Payments will be made only for the quantity calculated by the difference between founding level and spot/grid level multiplied by PCC area.
1.1.1 | a) From existing ground level to a depth of 3 m | Cum | 15255
1.1.2 | b) Depth above 3.00 m | Cum | RO
Rate to include necessary manual excavation for dressing the edges and levelling, spreading the earth in layers to the required levels within the site, watering, consolidation, dewatering of surface / rain water, dumping surplus earth outside the site by manual / mechanical means, the alloted location by client within 2Km Radius and carting away the excess soil including necessary loading and unloading to a place not objected by Authorities.
1.2 | Specification and scope of work same as item no (1.01) but for unpoclainable hard rock / boulders (more than 1/2 cum in size) by chiselling / wedging. | Cum | 0
1.3 | Back filling: Back filling of earth / soil including breaking clods, watering and consolidating in 150mm thick layers, compacting each layer with vibratory compactor and at inaccessible places with wooden / steel rammers to achieve 98% standard proctor density at optimum moisture content for retaining wall, lift pits, sump tank, above raft slab, and else where as directed by the Engineer.Payments will be made only for the quantity calculated by the difference between founding level and spot/grid level multiplied by PCC area by deducting PCC/RCC quantity
1.3.1 | a) Earth / soil available at site | Cum | 10190
1.3.2 | b) Approved earth / soil brought from outside | Cum | RO
1.3.3 | c) Quarry Dust filling | Cum | RO
1.4 | Anti termite treatment: Providing Anti termite treatment in accordance with IS 6313 - part II by approved agency with minimum of 10 years of guarantee including the cost of chemical, precautionary measures etc complete.Only plan area shall be measured for payment. Contractor shall submit the method statement to the Engineer for approval. | Sqm | 4750
1.5 | Polythene Sheet: Providing and laying 150 micron gauge polythene paper/Polythene sheet below Grade slab, P.C.C, Raft slab etc, to required levels. For Payments only the plan area will be measured . Rate shall include supply, loading and unloading, storing, transportation, laying, sealing of junctions and overlaps etc complete as per the instructions of the Engineer. | Sqm | 4750
Total for Excavation & Filling (i)
2 | PLAIN CEMENT CONCRETE:
2.1 | Providing and laying PCC of M 10 grade with mix proportion, 1:3:6 for foundations using graded granite aggregate of 40mm and down size including machine, mixing, compacted by wooden or cast iron rammers, curing etc., complete. | cum | 635
Total for PCC (ii)
3 | REINFORCED CEMENT CONCRETE
Important notes in regard to reinforced cement concrete.
1. All concrete used for reinforced concrete work (structural concrete) shall be "Controlled concrete" and the use of weight batching is a must and shall be insisted upon.
While quoting for structural concrete work contractors are particularly advised to study the relevant drawings carefully before quoting.
Contractors shall submit drawings showing the scheme of form work (shuttering) for beams and slabs, areas which project out at various levels as indicated in drawings and this shall be obligatory.
The successful tenderer shall maintain at site, cube testing machine in good working order, sieves, slump cone, graduated cylinder and weights, scales for material testing.
NOTE: A qualified mechanic shall always be available during working hours for maintenance of weight batching machines.
Providing & laying controlled reinforced cement concrete conforming to grades as specified in (IS 456 - 2000) as per specifications using 20mm down size aggregates at any depth or heights and the rates are excluding the reinforcement steel and shuttering(formwork). The rate shall include for stagging/scaffolding, compacting with vibrators,curing,hacking(wherever required) and providing recess to walls or columns, sleeves in slabs, construction joints sunk slabs, cantilever slabs, making holes or cutting formwork for taking out Electrical conduits or dowels for column to Brick work, to the required shape, size, slope shown in drawings for the following items of work.
Nitto Bond EP based application shall be provided for the construction joints.
Contractors shall submit drawings showing the scheme of formwork (shuttering) for all items of work detailed as under.
Formwork shall be designed for rigidity, durability, strength, water tightness, easy removal etc.,
Formwork designed with proposed materials (to be approved prior to making) shall be able to retain its shape, line, dimension, level within the allowable limits of variations. Props shall be only steel props.
Necessary arrangement shall be envisaged to provide camber in beams or slabs as per design.
Formwork for construction joints shall be submitted for approval.
NOTE :
1 | For all Concrete works to be done from Batching Plant with Minimum Capacity of 30 cum /hr.
2 | Tower Crane to be Considered total height of the building
3 | Design mix shall be as approved by the Structural Consultant
4 | Test Lab Site has to be set up to test samples at regular intervels and as instructed by Stuctural Consultants .
5 | All RCC elements should be water leak proof structure and the contractor ensure the same.
6 | The minimum cement contents for different grades of concrete and using 53 grade of cement shall be as follows:
Grade of Concrete -- OPC 53 grade Cement
M10 -- 210Kg/Cum
M20 -- 300Kg/Cum
M25 -- 300Kg/Cum
M30 -- 320Kg/Cum
M35 -- 340Kg/Cum
M40 -- 360Kg/Cum
M45 -- 380Kg/Cum
Minimum cement content of concrete mentioned are of Guidance purpose only and the same shall be confirmed with trail Mix and Cube Teat as per relevant IS standard
RMC /Batching Plant Concrete for below mentioned works
3.1 | In Foundation
3.1.1 | Raft (M30) | Cum | 2500
3.1.2 | Footings (M30) | Cum | 300
3.1.3 | Grade slab (M25) | Cum | 635
M30 Concrete Grade
3.2 | Pedestals | Cum | 55
3.3 | Plinth Beams | Cum | 300
3.4 | Columns | Cum | 910
3.5 | RC Walls | Cum | 445
3.6 | RC Beams | Cum | 1810
3.7 | RC Slab | Cum | 3035
3.8 | Stair Case | Cum | 430
3.9 | Turn Down | Cum | 30
Total for RCC (iii)
4 | FORM WORK/SHUTTERING
Providing, erecting, laying & fixing of suitable Centering / Shuttering / staging / form work systems as temporary works for execution of permanent works at all levels for the following works including strutting, propping, bracing, staging, moulding, de-moulding, deshuttering, etc., using approved formwork systems including transportation, shifting the materials from yard to place of work, assembling, multiple handling of the materials with necessary consumables such as nails, screws, binding wires, fasteners, tools and tackels etc complete. Cost to include sealing the joints in the formwork system with heavy duty adhesive tape, sealers, applying mould releasing agents, aligning to required line and levels including MS ties, concrete cover blocks spacers etc., complete.
Unless otherwise specified rates quoted for all Form works shall include the following :
Cost of all materials, labour, equipment / tools & plants required, lead and lifts, conveyance, infrastructure facilities required etc. Form work shall include splayed edges, notching, allowances for overlaps and passing at angles, batterns, strutting, bolting, wedging, casing, rocking, centering, boxing, shuttering, propping strut braces etc., removal thereof and coating the shuttering with releasing agent /oil to prevent cement sticking to shutter faces. Form work shall be either straight, curved, plain or tapered and also with provision for specified slopes, if directed. Wind tie bolts for wall shuttering.
Cost of suitable framework and bracing according to the floor height specified in the drawing, moulds, centering and shuttering, single / double height scaffolding, as directed at site. Dimension of form work will be within the tolerance as specified in IS 456 and shuttering should be water tight. Shuttering materials shall be Aluminum / steel / timber or plywood as suitable for the work intended.
Tenderer shall ensure that they have adequate quantity of shuttering and suitable propping materials according to the floor height specified in the drawing to keep up the required Concreting cycle per floor as set out in the Tender Documents, Drawings and Programme. They shall also ensure that the de-shuttering sequence with proper propping, taking into account the Construction Loading of the upper slabs, as set out in the Tender Drawings, is also kept up. Scheme to maintain the props shall ensure that main supports are not disturbed. Reproping by means of removal and reintroducing of props is not allowed.
Formwork for construction joints shall be submitted for approval. Shuttering below the shrinkage strip at every level shall be retained in place without disturbing for a time as specified by the structural engineer. Any honey combs, any undulations, bulging, any leakage of slurry, concrete etc is not acceptable and decision of the structural consultant along with the architect is final. All necessary treatment to honey combed areas, uneven concrete surfaces shall be made proper as per the Engineer without any extra cost.
Formwork shall be designed for close jointed rigid, durable and shall have adequate strength, water tightness and ensure easy removal etc., Props, shorings and bracings shall be all in steel. Formwork designed with proposed materials (to be approved prior to making) shall be able to retain its shape, line, dimension, level within the allowable limits of variations. Necessary arrangement shall be envisaged to provide camber in beams or slabs as per design.
Contractor is responsible for the correctness and stability of the temporary works required for the permanent works. All design parameters including design details, shop drawings, method statements and material test certificates from external approved repuated testing laboratory shall be submitted to the consultant.
Exposed surfaces shall be free of blamish, residues of curing compound, uniform in colour, free of construction joint except detailed or approved under methodology of construction, forming construction joint or as providing joint free/ hole free water retaining structures. All system to have in built supporting safety screens.
All tie rod holes to be filled with approved grouting material. Cost to include necessary embedded tie rod for fixing the one sided shuttering and water retaining structures.
Shuttering & deshuttering sequence shall be 100%, 80% & 40% from the slab to be cast respectively depending on the progress. The same is as per the details enumerated in General Notes. Contractors shall submit drawings showing the scheme of formwork including back propping and proper sequence of removal of formwork and back propping so that the structural slab will not be overloaded due to construction loads. All slabs shall be progressively DE shuttered and back propped. It is compulsory to provide adequate back props to the slab on which the supports are resting before taking up concreting work for every slab.
Minimum of 150mm high MS frame works is required for kickers and starters in case required and formwork design calculations including re-propping arrangements needs to be submitted for approval.
Providing 2mm thick foam sheet at joints to prevent leakage of slurry during compaction, removing adhesive tape from concrete surface if any after deshuttering
Formwork for construction joints shall be submitted for approval. Shuttering below the shrinkage strip at every level shall be retained in place without disturbing for a time as specified by the structural engineer.
Additional height beyond 5 m @ various levels shall be paid under relavant item. Kindly refer the architecture layouts.
Form work concrete items shall be of film faced marine plywood of approved make in any size required for the purpose under such item, fixed on suitable framework including MS clear separators, if so specified.
Form work for fair faced concrete items Y columns, voided slab will be of resin bonded plywood of approved make in any size required for the purpose under such item, fixed on suitable framework including MS clear separators, if so specified.
Formwork design shall be in contractor's scope & shall be submitted with shop drawings for structural consultant review & obtain written approval for the same prior to execution at site
All Form works shall be done in accordance with technical specification Division 3 Section 03350
4.1 | In Foundation
4.1.1 | Isolated & Combined Footings, Raft | Sqm | 835
4.2 | Pedestals | Sqm | 345
4.3 | Plinth Beams | Sqm | 2560
4.4 | Columns | Sqm | 11585
4.5 | RC Walls | Sqm | 4400
4.6 | RC Beams | Sqm | 20255
4.7 | RC Slab | Sqm | 20000
4.8 | Stair Case | Sqm | 3850
4.9 | Turn Down | Sqm | 210
4.1 | Extra for additional height in centering, shuttering where ever required with adequate bracing, propping etc., including cost of de-shuttering and decentering at all levels, over a height of 5m, for every additional height of 1 metre or part thereof (Plan area to be measured). | Sqm | 315
Total for Form work (iv)
5 | REINFORCEMENT STEEL WORKS
Unless otherwise specified rates quoted for all Reinforcement works shall include the following :
Work at any depth below ground level or any height above ground level and at all levels, heights & elevation and location.
All reinforcement steel shall be from the primary steel ingots qualifying IS 1786.
Supply, Cutting, wastage, straightening, bending, hoisting, fixing, supporting in position using cover/spacer blocks and tying with approved binding wire made out of 18 gauge G.I. annealed wire using either conventional hook or hand twister or automatic tying machine or fusion welding whichever is appropriate adopting various knots required for rigidity and positioning of the bars.
All reinforcement steel shall be cut & bent to the required size and shape as detailed in the structural drawings using necessary plants & machinery in the factory/ site and all lapping for 16mm and above in columns, corewalls, shearwalls & staircase walls shall be using mechanical threaded couplers as per the code. For all other elements lap length shall be considered as per structural drawings & details.
Quantity of steel shall be as per drawing and authorised overlaps only shall be measured and paid. Contractor shall prepare bar bending schedule and fabrication shall be carried out as per approved bar bending schedules/fabrication drawing. All testing including physical & chemical and quality assurances shall be as per the tender conditions / Specifications and no extra shall be paid for the same.
Unless otherwise noted in the bills of Quantities, method of measurements shall be generally in accordance with IS 1200. Reinforcement shall be measured only in lengths of bars as actually placed in position on standard weight basis, no allowance being made in the weight for rolling margin. Authorised laps and splices only will be measured. Chairs of any shape & profile, Spacer bar of any shape & profile, cover block, wastage and binding wire will not be measured and shall be included in the quoted rates.
Tests on materials shall conform to IS Specification and the test shall be carried out for each loads and the parameter test reports shall be submitted as per structural consultant requirement, either at site Laboratory or at any approved test laboratory.
Quoted rate to include lead, lift, necessary fixing and tying arrangements for dowel bars, protection to dowel bars rebending of dowel bars, placing at all levels and as directed.
All Reinforcement steel works shall be done in accordance with technical specification Division 3 Section 03400.
5.1 | REINFORCING STEEL
Providing, fabricating & fixing in position reinforcement steel for RCC works for bar of various diameters and grade of steel at all levels conforming to IS specification including transporting from yard, de coiling, straightening, cutting, bending, hoisting, fabricating, and placing in position according to drawings and binding the reinforcement with MS annealed binding wire of double fold of 18 gauge and providing PVC cover blocks, for placing the reinforcements in position and for maintaining the cover specified and/or according to relevant IS including dewatering wherever necessary. The rate shall include cost of binding wire and spacers bars which will not be measured separately for payment etc complete all as per design, specifications and drawings, with all lead & lift for all materials & labour and as directed, at all heights & locations. The amount for the chairs shall be paid extra as per the actual , quantities measured & approved by the client representative. Only approved lap length as per the drawings shall be measured for payment. Welding is allowed for the lapping & is to be followed as per IS 2751 and IS9417. Client & TRC approved steel brands include SAIL, TATA & JSW makes. Contractor shall prepare bar bending schedule and fabrication shall be carried out as per bar bending schedules. (Note: All testing (including physical & chemical) and quality assurances shall be as per the tender conditions/ Specifications and no extra shall be paid for the same.)
5.1.1 | High yield strength deformed bars conforming to Fe 500 N/mm2 | MT | 1400
Total for Reinforcement Steel (v)
6 | WATERPROOFING WORKS
Waterproofing General Notes: a) The Contractor shall obtain approval of the Engineer for the agency for water proofing. b) The Contractor shall give guarantee for ten (10) years for the water proofing from the date of issue of substantial completion certificate. c) The Contractor shall arrange manufacturer's guarantee for ten (10) years or as approved by the Employer. d) The Contractor shall submit method statement along with the makes considered, including sketch and shall obtain Engineer's approval. e) Quoted rates shall include all leads, lifts, scaffolding and curing. f) The Contractor shall clean all the surfaces and make it free of dust, oil and other contaminants, remove sharp projections, moss and lichen, treat with fungicidal wash to inhibit further growth, pressure grout construction joints and honeycomb areas with cement grout, prepare concrete surface by mechanical means/ hydro blasting to ensure a good bond between the topping and the substrata. g) The Contractor shall test the surfaces prior to start of work by ponding for 24 hours, and take remedial measures as approved by the Engineer. h) After one month of completion, the Contractor shall carry out 24 hour ponding test again, as directed by the Engineer. i) Making watta at corners/ junctions etc. shall be included in the rates. j) Rate to be inclusive of tie rod grouting and packing with approved method where ever applicable. k) Mode of Measurement shall be actual area treated.
6.1 | Crystalline Hydrophilic waterproof coating system
Providing and Applying a waterproof, efflorosence -free, levelling and protective weather resisitant render layer of Min 3mm thick, comprising of cements, quartz with graded size distribution and special additives, to be manually applied by trowel or can also be applied by spray application for speedier completion of the work for larger areas. The product/system must be UV resistant, non toxic, Environment friendly, white in colour, have a high impact resistance, with a maximum aggregate size of 0.4mm . The Product/system shall be applied in 2 or 3 coats as required , with a min total consumption of 6 kg/m2 to achieve a total thickness of Min 3mm, all as per manufacturers recommendations , etc complete. The product conforms to Min compressive strength > 30 Mpa at 28 days ageing, Adhesion to concrete surfaces shall be min 2 N/mm2 as per EN 1504-3, and Reaction to fire as per EN 13501-1( Euroclass) conforming to A1. The vertical surface/ horizontal surface of the concrete shall be taken up for thorough surface preparation with compressed air blowing and mechanical removal of debris, laitance, etc. Surface prepared shall be comply to ICRI- CSP 2 requirements.
3mm thick DFT
6.1.1 | Foundations | Sqm | 470
6.1.2 | Lift pits -Floors & Walls | Sqm | 325
6.2 | Wet Areas/Toilets/Balcony/Utility
Waterproofing system: Providing and applying two component high performance polymer modified cementitious waterproofing coating, having minimum elongation of 120%, Tensile strength 1 N/mm2 (As per ASTM D412), Water Vapour Transmission 0.7 Perms (As per ASTM E96), Adhesion Strength 1 Mpa (As per ASTM D 7234), Crack bridging up to 2mm (As per ASTM C836) and food grade certification by CFTRI, including reinforcing the coating with 45gsm glass fibre mesh at all corners. The coating shall be applied with a total consumption of 2 Kg/Sqm in two coats on the entire horizontal and vertical surface as per manufacturer's specification and methodology. The system includes base preparation of cleaning, brushing and removal of flacky materials, grouting the porous area with cementitious grout, sealing the minor cracks, proper covering between slab and wall junctions and pre-wetting the surface to attain SSD condition before application of the waterproofing coating, followed by the application of waterproof coating.
6.2.1 | Toilets | Sqm | 3300
6.2.2 | Horizontal protection: Supplying and applying slope making protection with 40 mm avg thick M20 grade fibrated screed as per the site requirement. | Sqm | 3230
6.2.3 | Vertical protection: Supplying and applying 15mm thick polymeric waterproof plastering with CM 1:4 admixed with integral waterproofing compound at 0.2litre/bag of cement. | Sqm | 860
6.3 | Terrace Waterproofing
Providing and applying 2 component liquid applied, high build elastomeric polyurethane waterproofing system which complies to ASTM C 836 for the minimum thickness of 1.5 mm DFT. This shall be applied at a coverage @ 2.0-2.1 kg/m2 to achieve minimum DFT of 1.5 mm using metal scrapper. The coating shall be applied on the entire horizontal surface and 300mm above FFL on vertical surface. The product shall be exhibiting properties i.e. Solids by Volume : 98%, Tensile strength (ASTM D412) : >6 N/mm2, Elongation (ASTM D412) : >600%, Tear Resistance (ASTM D624) : 35 N/mm, Shore A Hardness (ASTM D2240): 70, Bond Strength to concrete (ASTM D 7234) - >1.5 Mpa, Crack Bridging ability(Static) (EN 1062-7)- > 3.5 mm, Puncture Resistance (ASTM E154) - > 300 N, Resistance to hydrostatic head (ASTM D5385) - > 70 Mtr, Root Resistance (CEN TS/14416) : Pass & Dynamic Crack Bridging (EN 1062-7, Method B-B 3.2) 20000 cycles at (-20 °C): Pass. The system includes base preparation of cleaning, brushing and removal of flacky materials, grouting the porous area with cementitious grout, priming the surface with moisture insensitive epoxy primer applied with a total consumption of 200 gms/Sqm, followed by application of polyurethane coating in one or two coats.
6.3.1 | Terrace Waterproofing | Sqm | 4550
6.3.2 | Protection to the waterproofing system: Supplying and applying protective geo textile fabric of 120 GSM over the entire membrane with proper overlaps. | Sqm | 4550
6.3.3 | Horizontal Protection: Supplying and applying an average of 75mm thick M20 fibrated grade concrete screed including saw cutting (approx. 6mm W x 10 mm D) at 3MX4M panels and filling the groove with PU sealant, and making angle fillet of 100mmX100mm using M20 grade concrete at the corners. | Sqm | 4460
6.3.4 | Vertical protection: Supplying and applying 15mm thick polymeric waterproof plastering with CM 1:4 admixed with integral waterproofing compound at 0.2litre/bag of cement. | Sqm | 330
Total for Water Proofing (vi)
GRAND TOTAL Structure works (I) ( i to vi)
(II) | CIVIL WORKS
7 | MASONRY WORKS
Note:
Unless otherwise specified, the rates quoted for all items shall include the following.
1. All scaffolding, ladder, platforms, staging and plant required in the execution of the work any height or depth.
2. Hacking or roughening of concrete or other surface in contact with masonry for bondage.
3. Raking out joints to specified depth either for plastering or pointing.
4. Levelling and preparing top of masonry damp proof course.
5. Building in holdfasts and such other inserts.
6. Keeping the work well wetted for two weeks.
7. Work at all heights, depths unless otherwise specified.
8. Any items in this head having concrete work shall be paid for under "CONCRETE" head only.
9. Rate quoted for 100 / 115 mm thick masonry to include provision of 100 / 115 x 75 mm horizontal R.C.C stiffeners at 1.0 mts vertical intervals
10. LEED REQUIREMENTS:- 1.Cement shall have 25% Fly Ash Content (PCC) and also shall be procured within 400kms of the project site. 2. 200mm Size Stone shall be procured within 400kms of the project site.
7.1 | Providing and constructing Solid Cement Concrete block masonry in cement mortar 1:6 (1 cement : 6 coarse sand) using factory made, load bearing, approved quality, Grade D (4.0) Density of blocks not less than 1800 kg/cum. Minimum average compressive strength of units 4.0 N/sqmm and minimum strength of individual unit is 3.2 N/sqmm, set to level plumb including setting in position, providing scaffolding, curing, raking out joints wherever necessary etc., complete with all leads and all as per specification and direction of Architect / Engineer-in-charge in super structure. 100mm Bonding bar fixed to a concrete column at every fourth course of blockwork.
For 200mm thick walls using (400x200x200)mm size blocks
7.1.1 | Ground Floor | sqm | 5542.149
7.1.2 | First Floor | sqm | 5045.4131
7.1.3 | Second Floor | sqm | 4156.988
7.1.4 | Third Floor | sqm | 4222.2532
7.1.5 | Fourth Floor | sqm | 7153.4793
7.1.6 | Fifth Floor | sqm | 4132.3216
7.1.7 | Sixth Floor | sqm | 4195.2592
7.1.8 | Terrace Floor | sqm | 2916.2686
7.2 | Providing and constructing Solid Cement Concrete block masonry in cement mortar 1:6 (1 cement : 6 coarse sand) using factory made, load bearing, approved quality, Grade D (4.0) Density of blocks not less than 1800 kg/cum. Minimum average compressive strength of units 4.0 N/sqmm and minimum strength of individual unit is 3.2 N/sqmm, set to level plumb including setting in position, providing scaffolding, curing, raking out joints wherever necessary etc., complete with all leads and all as per specification and direction of Engineer-in-charge. 100mm Bonding bar fixed to a concrete column at every fourth course of blockwork.
For 150mm thick walls using (400x150x200)mm Size blocks
7.2.1 | Ground Floor | sqm | 318.7575
7.2.2 | First Floor | sqm | 239.811
7.2.3 | Second Floor | sqm | 239.5151
7.2.4 | Third Floor | sqm | 211.728
7.2.5 | Fourth Floor | sqm | 200.8215
7.2.6 | Fifth Floor | sqm | 245.6135
7.2.7 | Sixth Floor | sqm | 245.6135
7.3 | Providing and constructing solid cement concrete block masonry in cement mortar 1:4 (1 cement : 4 coarse sand) in superstructure using factory made load bearing approved quality cement concrete blocks of specified size, Grade D(4.0), Density of blocks not less than 1800kg/cum Minimum average compressive strength of units is 4.0 N/sqmm and minimum strength of individual unit is 3.20N/sqmm, set to level, plumb, setting in position, providing scaffolding, curing, raking out joints wherever required etc., complete including providing RCC 1:2:4 (1 cement :2 sand : 4 graded stone aggregate of 20mm nominal size) - stiffeners of size 100mmx75mm at every 900mm centers including formwork, MS reinforcement consisting of 2 nos. of 6mm dia MS bars for main reinforcement with 6mm dia MS links at 230mm c/c for each RCC stiffener etc., complete all as per specifications and directions of Engineer in charge. 100mm Bonding bar fixed to a concrete column at every fourth course of brickwork.
| For 100mm thick partition wall using (400x100x200)mm Size blocks | sqm | RO
SUB TOTAL OF MASONRY WORK (i)
8 | PLASTERING WORKS
Note:
1. Hacking or scarifying concrete surface to be plastered or rendered.
2. Preparation of surfaces by raking of joints wetting the surface,etc.,
3. Providing grooves at the junction of masonry and concrete members wherever different materials are connected and also wherever necessary.
4. Work at all heights and depths.
5. Providing drip moulds wherever necessary.
6. Washing floors, cleaning glass and leaving premises clean and tidy.
7. Curing.
8. Necessary scaffolding, ladder platform for any height and depth.
9. Providing Plaster mesh and Corner bead to junction of masonry and concrete members and masonry edges wherever different materials are connected all as directed.
10.Any items in this head having concrete work shall be paid for under CONCRETE head only.
11.Fine aggregate should be sieved sand less than 3.0mm for the plastering work.
12. All work to be finished smooth to required line & level, plumb, round in of corners wherever required.
13. Cost to include all lead & lifts.
14. LEED REQUIRMENTS:- 1.Cement shall have 25% Fly Ash Content (PCC) and also shall be procured within 400kms of the project site.
8.1 | Plastering 12mm / 15mm thick with cement mortar specified below, finished smooth, including scaffolding, curing, etc.; complete for INTERNAL SURFACES of walls, beam, ribs, sills, jambs, ceiling, etc.; complete all as per specifications at all heights. Mix specified is for cement : fine sand. River sand to be used.
8.1.1 | For Internal Walls with CM 1:6. (15mm thk)
8.1.1.1 | Ground Floor | sqm | 11246.3766
8.1.1.2 | First Floor | sqm | 11598.2531
8.1.1.3 | Second Floor | sqm | 9157.7132
8.1.1.4 | Third Floor | sqm | 8961.1111
8.1.1.5 | Fourth Floor | sqm | 8730.278
8.1.1.6 | Fifth Floor | sqm | 9350.3441
8.1.1.7 | Sixth Floor | sqm | 9188.7325
8.1.1.8 | Terrace Floor | sqm | 2384.56
8.1.2 | For Ceiling with C.M 1:4. (12mm thk)
8.1.2.1 | Ground Floor | sqm | 4013.9473
8.1.2.2 | First Floor | sqm | 3885.3444
8.1.2.3 | Second Floor | sqm | 2973.4588
8.1.2.4 | Third Floor | sqm | 2976.5564
8.1.2.5 | Fourth Floor | sqm | 2846.6556
8.1.2.6 | Fifth Floor | sqm | 3043.1636
8.1.2.7 | Sixth Floor | sqm | 2976.8732
8.1.2.8 | Terrace Floor | sqm | 326.072
8.2 | Plastering 12mm thick with cement mortar specified below, finished rough including scaffolding, curing, etc.; complete for CLADDING SURFACES inclusive of sills, jambs, soffits, ceilings, etc.; complete all as per specifications for heights up to 10m above GL. Mix specified is for cement : River sand to be used.
8.2.1 | in CM 1:4. Rough Plastering for Washroom dado
8.2.1.1 | Ground Floor | sqm | 1171.5334
8.2.1.2 | First Floor | sqm | 998.2694
8.2.1.3 | Second Floor | sqm | 816.0134
8.2.1.4 | Third Floor | sqm | 816.0134
8.2.1.5 | Fourth Floor | sqm | 816.0134
8.2.1.6 | Fifth Floor | sqm | 816.2774
8.2.1.7 | Sixth Floor | sqm | 816.2774
8.3 | Providing plastering 20mm thick with cement mortar 1:5 finished smooth including scaffolding, cost of materials, labour curing, etc.; complete for EXTERNAL SURFACES of stone masonry / RCC wall / brick masonry walls, sills, jambs, soffits, etc.; complete all as per specifications and detailed drawings for all heights above GL. Mix specified is for cement : Coarse Sand. Rate to include providing polymeric waterproof plastering admixed with integral waterproofing compound at 0.2litre/bag of cement in cement plaster work or in proportion recommended by the manufacturers.
8.3.1 | External wall surface in CM 1:5.
8.3.1.1 | Ground Floor | sqm | 4567.3861
8.3.1.2 | First Floor | sqm | 4849.44
8.3.1.3 | Second Floor | sqm | 3789.192
8.3.1.4 | Third Floor | sqm | 3490.476
8.3.1.5 | Fourth Floor | sqm | 3556.6773
8.3.1.6 | Fifth Floor | sqm | 3548.0742
8.3.1.7 | Sixth Floor | sqm | 3548.0742
8.3.1.8 | Terrace Floor | sqm | 4746.2192
SUB TOTAL OF PLASTERING WORKS (ii)
9 | MISCELLANEOUS WORKS
9.1 | Providing and filling Cinder Filling in sunken portions, well mixed, consolidated by tamping, top surface finished to receive flooring as directed etc., complete. a) Supplying approved quality cinder / lightweight aggregate free from dust, organic impurities, or oversized particles for bathroom sunken applications. b) Carefully spreading the cinder over the waterproofed sunken slab to the required thickness (40–60 mm or as per drawing) without causing any damage to the waterproofing layer. c) Levelling the cinder manually, maintaining the required floor profile for further screed concreting. d) Light compaction of the cinder using hand rammers to obtain a stable and even substrate, ensuring no point loads or damage to the waterproofing membrane. e) Filling neatly around pipe risers, junctions, and wall edges to avoid voids or pockets.
Cinder Filling for Sunken Slabs @ Washrooms
9.1.1 | Ground Floor | Cum | 186.618
9.2 | Providing and finishing the surface of the cinder filled area with screed concrete to receive the tiling etc., complete a) Providing and laying cement concrete screed (M15 / 1:2:4) over the compacted cinder filling to an average thickness as specified to achieve required slopes towards the floor traps. b) Placing concrete using screed battens / guides to maintain proper gradients ensuring smooth flow of water to the drain. c) Compacting the concrete thoroughly using manual tamping to avoid honeycombing and to create a firm substrate for tile fixing. d) Forming rounded coves (75×75 mm) at all wall–floor junctions using cement mortar to prevent water stagnation and facilitate waterproofing continuity. e) Finishing the screed surface with wooden float / trowel to receive tile adhesive and floor tiles. f) Curing the screed concrete using wet hessian / sprinkling water for a minimum of 3–5 days depending on site conditions.
Screed Concrete above Cinder Filling @ Washrooms
9.2.1 | Ground Floor | Sqm | 31.103
SUB TOTAL OF MISCELLANEOUS WORKS (iii)
GRAND TOTAL Civil Works (II) (i to iii)
(III) | ELECTRICAL WORKS
(IIIA) | ELECTRICAL WORKS (HOSTEL BLOCKS)
PART 'A' - INTERNAL CABLE WORK
10 | Supply, Installation, Testing & Commissioning of 1100V grade, Aluminum / copper conductor, PVC / XLPE Insulated & galvainsed steel tape armouring .The cable shall be heavy duty type conforming to IS-1554 & 7098. The cable shall be suitable to lay directly underground in Existing trenches/ RCC Ducts/Sleeves/ Cable trays. Rate shall be excluding of cabling laying related civil work.
(A) | Aluminium Armoured XLPE Insulated cables
10.1 | Supply & Installation of 3.5C X 50 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 420
| Installation | Mtrs. | 420
10.2 | Supply & Installation of 3.5C X95 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 100
| Installation | Mtrs. | 100
10.3 | Supply & Installation of 3.5C X150 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 0
| Installation | Mtrs. | 0
10.4 | Supply & Installation of 3.5C X 120 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 140
| Installation | Mtrs. | 140
10.5 | Supply & Installation of 3.5C X 185 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 160
| Installation | Mtrs. | 160
10.6 | Supply & Installation of 3.5C X 70 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
10.7 | Supply & Installation of 4C X 50 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 240
| Installation | Mtrs. | 240
10.8 | Supply & Installation of 4C X 35 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 240
| Installation | Mtrs. | 240
10.9 | Supply & Installation of 4C X 25 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
10.10. | Supply & Installation of 4C X 16 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
10.11 | Supply & Installation of 4C X 10 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
A1 | Armoued Copper Cable
11 | Supply & Installation of 4C X 16 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 1116
| Installation | Mtrs. | 1116
11.1 | Supply & Installation of 4C X 10 Sq mm Cu XLPE Armoured cables
| Supply | Mtrs. | 712
| Installation | Mtrs. | 712
11.2 | Supply & Installation of 4C X 6 Sq mm Cu XLPE Armoured cables
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
11.3 | Supply & Installation of 4C X 4 Sq mm Cu XLPE Armoured cables
| Supply | Mtrs. | 420
| Installation | Mtrs. | 420
11.4 | Supply & Installation of 3C X 4 Sq mm Cu XLPE Armoured cables
| Supply | Mtrs. | 736
| Installation | Mtrs. | 736
11.5 | Supply & Installation of 4C X 2.5 Sq mm Cu XLPE Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
11.6 | Supply & Installation of 3C X 2.5 Sq mm Cu XLPE Armoured cables
| Supply | Mtrs. | 312
| Installation | Mtrs. | 312
(B) | Single Core PVC insulated Flexible Copper cable.(IS 694:1990)
11.7 | Supply & Installation of 1C X 10 sq mm Copper Flexible Cable
| Supply | Mtrs. | 1500
| Installation | Mtrs. | 1500
11.8 | Supply & Installation of 1C X 16 sq mm Copper Un. armoured Cable
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
(C) | Flexible Copper Wire
11.9 | Supply & Installation of 4RX6 sq mm+2Rx2.5Sqmm Cu.flexible wire( pantry DB)+ LDB+Power DB with 32 dia conduit
| Supply | Mtrs. | 1428
| Installation | Mtrs. | 1428
11.10. | Supply & Installation of 4RX4 sq mm+1Rx2.5Sqmm Cu.flexible wire( LDB) with 32 dia conduit
| Supply | Mtrs. | 3752
| Installation | Mtrs. | 3752
11.11 | Supply & Installation of 4RX10 sq mm+2Rx4Sqmm Cu.flexible wire( lift) WITH 32 dia conduit
| Supply | Mtrs. | 1236
| Installation | Mtrs. | 1236
12 | End terminations & Gland Earthing
Supply, Installation, Testing & Commissioning of End terminations for cables with brass gland of Double / Single compression and copper lugs etc, complete as per specifications. Also Supply & Installation of Gland Earthing Conisting of Suitable ring and Brass Nuts, Bolts and washers. Cost of Aluminum engraving cable tag for incoming and out going cables shall be inclusive in rate.
Note:
1. Single compression brass gland should be provided for all type of multi core armoured cables of size below 95 Sq. mm.
2. Double compression brass gland should be provided for all type of multi core armoured cables of size including 95sqmm and above
3. PVC gland should be provided for single core & multi core flexible copper cables
4. Only copper lugs should be used for aluminum and copper armoured / unarmoured cables irrespective of sizes
(A) | Aluminium Armoured XLPE Insulated cable termination with copper lugs
12.1 | Supply & Installation of 3.5C X 120 Sq mm Aluminum Armoured cables
| Supply | Nos. | 8
| Installation | Nos. | 8
12.2 | Supply & Installation of 3.5C X 185 Sq mm Aluminum Armoured cables
| Supply | Nos. | 56
| Installation | Nos. | 56
12.3 | Supply & Installation of 3.5C X 70 Sq mm Aluminum Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
12.4 | Supply & Installation of 3.5C X 50 Sq mm Aluminum Armoured cables
| Supply | Nos. | 56
| Installation | Nos. | 56
12.5 | Supply & Installation of 4C X 35 Sq mm Aluminum Armoured cables
| Supply | Nos. | 8
| Installation | Nos. | 8
12.6 | Supply & Installation of 4C X 25 Sq mm Aluminum Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
12.7 | Supply & Installation of 4C X 16 Sq mm Aluminum Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
12.8 | Supply & Installation of 4C X 10 Sq mm Aluminum Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
12.9 | Supply & Installation of 3.5C X150 Sq mm Aluminum Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
12.10. | Supply & Installation of 3.5C X95 Sq mm Aluminum Armoured cables
| Supply | Nos. | 8
| Installation | Nos. | 8
(B) | Copper Armoured XLPE/PVC Insulated cable termination with copper lugs
13 | 3C x 2.5 sqmm Copper Flexible Cbale for data Switch power supply
| Supply | Mtrs. | 312
| Installation | Mtrs. | 312
( C) | Supply & Installation of End terminations Flexible Copper cable - with copper lugs & thermoplastic/Polyamide Cable gland including lock nut.
13.1 | Supply & Installation of 1C X 16 sq mm Copper Flexible Cable
| Supply | Nos. | RO
| Installation | Nos. | RO
13.2 | Supply & Installation of 1C X 10 sq mm Copper Un. armoured Cable
| Supply | Nos. | 232
| Installation | Nos. | 232
(D) | Flexible Copper Wire
14.1 | Supply & Installation of 4RX6 sq mm+2Rx2.5Sqmm Cu.flexible wire set with gland
| Supply | Nos. | 112
| Installation | Nos. | 112
14.2 | Supply & Installation of 4RX4 sq mm+1Rx2.5Sqmm Cu.flexible wire( LDB)
| Supply | Nos. | 224
| Installation | Nos. | 224
14.3 | Supply & Installation of 4RX10 sq mm+2Rx4Sqmm Cu.flexible wire( lift)
| Supply | Nos. | 40
| Installation | Nos. | 40
A1 | Armoued Copper Cable
15.1 | Supply & Installation of 4C X 16 Sq mm Cu XLPE Armoured cables
| Supply | Nos | 112
| Installation | Nos | 112
15.2 | Supply & Installation of 4C X 10 Sq mm Cu XLPE Armoured cables
| Supply | Nos | 64
| Installation | Nos | 64
15.3 | Supply & Installation of 4C X 6 Sq mm Cu XLPE Armoured cables
| Supply | Nos | 8
| Installation | Nos | 8
15.4 | Supply & Installation of 3C X 4 Sq mm Cu XLPE Armoured cables
| Supply | Nos | 56
| Installation | Nos | 56
15.5 | Supply & Installation of 4C X 2.5 Sq mm Cu XLPE Armoured cables
| Supply | Nos | RO
| Installation | Nos | RO
15.6 | Supply & Installation of 3C X 2.5 Sq mm Cu XLPE Armoured cables
| Supply | Nos | RO
| Installation | Nos | RO
15.7 | Supply & Installation of 4C X 4 Sq mm Cu XLPE Armoured cables
| Supply | Nos | 56
| Installation | Nos | 56
16 | CABLE TRAY
Supply & Installation of Factory made GI sheet metal type cable trays made out of 2mm thick . The cable tray shall be supplied as specified with necessary supports, all accessories like bend, Tees etc manufactured at the manufacturers work as per Drawing and required at site condition. The tray should be provided with adequate supports, the distance supports shall not be more than 1.2 to 1.5 meter . Coupler plate & galvanized hardware should be used to join the cable tray section. Earthing continuity shall be ensured at each joint. Cost to include the rate of ceiling supports also. (Cable trays should be Welded type)
( A ) | GI Ladder type cable trays
16.1 | 600mm wide with 75 mm depth Light duty 2 mm thick Ladder type cable trays
| Supply | Mtrs. | 136
| Installation | Mtrs. | 136
16.2 | 450mm wide with 50 mm depth Light duty 2 mm thick Ladder type cable trays
| Supply | Mtrs. | 100
| Installation | Mtrs. | 100
16.3 | 300mm wide with 50 mm depth Light duty 1.6 mm thick Ladder type cable trays
| Supply | Mtrs. | 464
| Installation | Mtrs. | 464
16.4 | 150mm wide with 50 mm depth Light duty 1.6 mm thick Ladder type cable trays
| Supply | Mtrs. | 112
| Installation | Mtrs. | 112
16.5 | 450mm wide with 75 mm depth Light duty 2 mm thick Hot dip galvanized Ladder type cable trays with cover 1.6mm thick and floor supports for terrace floor electrical works
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
16.6 | 300mm wide with 50 mm depth Light duty 2 mm thick Hot dip galvanized Ladder type cable trays with cover 1.6mm thick and floor supports for terrace floor electrical works
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
16.7 | 150mm wide with 50 mm depth Light duty 2 mm thick Hot dip galvanized Ladder type cable trays with cover 1.6mm thick and floor supports for terrace floor electrical works
| Supply | Mtrs. | 280
| Installation | Mtrs. | 280
16.8 | 100mm x 100mm U PVC trunking for DB dressing make: Precision make
| Supply | Mtrs. | 240
| Installation | Mtrs. | 240
16.9 | 450x75mm wide depth openable race way 2 mm thick with all fixing accessories cable trays with cover 1.6mm thick and floor/wall supports Data abling works
| Supply | Mtrs. | 160
| Installation | Mtrs. | 160
17 | 300x75mm wide depth openable race way 2 mm thick with all fixing accessories cable trays with cover 1.6mm thick and floor/wall supports Data abling works
| Supply | Mtrs. | 80
| Installation | Mtrs. | 80
TOTAL Internal cable works PART - A
PART - B : DISTRIBUTION BOARDS.
18 | Supply, Installation, Testing and commissioning of Distribution Boards, IP 43 (Double door) As per IS 2675 made out of 16swg GI sheet steel enclosure hinged GI cover/over flanged cover with cutouts for operating the MCB knobs and comprising of phase busbars, neutrals and earth bus with tapped holes, Bakelite phase shall be mounted by grouting in to the wall / angle to brick wall as required. DBs shall be suitable for single / three phase loads, Including fixing angle, DB termination lugs, PPI kits etc.
(Notes: Local fabrication Not permitted. Only factory made boxes shall be installed)
18.1 | 3ø, 4Way, ETPN DB with PPI KIT ( Room Lighting DB)
Incomers 1No. 25A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 25A, 30mA, DP, RCCB
12Nos. Of outgoing 6A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.2 | 3ø, 4Way, ETPN DB with PPI KIT ( Room Lighting DB)
Incomers 1No. 25A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 25A, 30mA, DP, RCCB
12Nos. Of outgoing 6A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.3 | 3ø, 4Way, ETPN DB with PPI KIT ( Room power DB)
Incomers 1No. 25A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 25A, 30mA, DP, RCCB
12Nos. Of outgoing 6A SP MCB With 'C' Curve
| Supply | Nos. | 56
| Installation | Nos. | 56
18.4 | 3ø, 6Way, ETPN DB with PPI KIT ( Common area LDB)
Incomers 1No. 25A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 25A, 30mA, DP, RCCB
12Nos. Of outgoing 6/10A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.5 | 3ø, 8Way, ETPN DB with PPI KIT ( Common area Power DB)
Incomers 1No. 40A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 40A, 30mA, DP, RCCB
18Nos. Of outgoing 16A /20A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.6 | 1ø,6/8WAY SPN DB ( UPS DB)
Incomers 1No.25A, DP, MCB 'D' Curve
4Nos. Of outgoing 10/6A SP MCB With 'D' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.7 | 1ø,12WAY SPN DB ( UPS DB)
Incomers 1No.25A, DP, RCCB 30 mA 'C' Curve
7Nos. Of outgoing 6A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.8 | Supply and installation of Din Rail Mounted 24Hr. Timer with 25A 2Pole contactor mounted in single Phase 8Way DB for aviation light with mast located at terrace floor. Make:Legrand,25A,004128 for aviation lighting.
| Supply | Nos. | 4
| Installation | Nos. | 4
18.9 | 1no. of 16amps, 1 phase industrial socket with plug controlled by 1no. Of 25amps (300mA) DP RCCB in IP65 enclosure
| Supply | Nos | 24
| Installation | Nos. | 24
18.10. | 3ø, 4Way, ETPN DB with PPI KIT ( Switch UPS DB )
Incomers 1No. 25A, 4P, MCB 'D' Curve
Phase outgoing 3Nos. 25A, 300mA, DP, RCCB A-S series
6Nos. of outgoing 10/16A SP MCB With 'D' Curve
| Supply | Nos. | RO
| Installation | Nos. | RO
18.11 | 3ø, 4Way, VTPN DB - FLOOR LIGHTING DB
Incomers 1No. 32A, 4P, MCB 'C' Curve
4Nos. Of outgoing 25 A TP MCB With 'C' Curve
| Supply | Nos. | RO
| Installation | Nos. | RO
18.12 | 3ø, 4Way, VTPN DB - ROOM FLOOR PDB
Incomers 1No. 32A, 4P, MCB 'C' Curve
4Nos. Of outgoing 25 A TP MCB With 'C' Curve
| Supply | Nos. | RO
| Installation | Nos. | RO
18.13 | 3ø6Way, ETPN DB with PPI KIT ( geyser)
Incomers 1No. 63A, 4P, MCB 'C' Curve
Phase outgoing 3Nos.63A, 30mA, DP, RCCB
12Nos. Of outgoing 16A /20A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
18.14 | 3ø,4Way, ETPN DB with PPI KIT ( Pantry DB)
Incomers 1No. 40A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 40A, 30mA, DP, RCCB
6Nos. Of outgoing 16A /20A SP MCB With 'C' Curve
| Supply | Nos. | 28
| Installation | Nos. | 28
TOTAL of distribution boards PART - B
PART - C : UPS AND ASSOCIATED WORKS
19.1 | Supply and installation of 10 KVA IGBT Based Online UPS System with 3 Phase input and 3 Phase output with MODBUS. The rate of UPS should include necessary accessories and base stand of height 300mm. Network interface card (RS485) suitable for modbus communication shall be provided along with UPS.
Make : Power One/Schneider/Emerson
| Supply | Nos | 4
| Installation | Nos. | 4
19.2 | Supply and installation of SMF Batteries to provide 15 Minutes Back Up with Battery Rack & Interconnecting Cables. 12V BATTERY
Make : Exide / Rocket / Client approved
| Supply | Sets | 4
| Installation | Sets | 4
TOTAL OF PART - C
PART - D : INTERNAL WIRING
( A) | Supply & Installation, Testing and Commissioning of point wiring using 2 x 1.5 + 1 R x 1.0 sqmm PVC insulated FRLS multi stranded 1100V grade copper wires drawn in 20mm dia 2mm thick PVC FRLS conduit including all conduit accessories such as bends, Junction boxes etc. The wiring shall be done in complete looping in system. The switches used shall be moulded on ORIENT MAKE MODEL SALUS Approved Make integral GI box with clear earthing facility. The wiring shall be complete with ceiling, switches and all consumables, connectors etc., The lighting circuit number to be placed in switch plate with sticker . (Colour coding of wiring should be adopted)
NOTE : ALL SWICTH AND SOCKET SHOULD BE ORIENT MAKE MODEL IS SALUS GREY ONLY
20.1 | One light point controlled by one switch considered as primary point. (Single Height area) {7 meters}
| Supply | Nos. | 1204
| Installation | Nos. | 1204
20.2 | For every additional secondary point. (Single height) {4meters} (General Lighting)
| Supply | Nos. | 1976
| Installation | Nos. | 1976
20.3 | Light points for staircase.(MCB Controlled ), consider cost of 4 module box with dummy plates.
| Supply | Nos. | RO
| Installation | Nos. | RO
20.4 | One Fan controlled by One no of One way switch with step type electronic regulator. {7 meters}
| Supply | Nos. | 156
| Installation | Nos. | 156
20.5 | exhaust fan point controlled by one switch near door along with socket considered as . (Single Height area) {7 meters}
| Supply | Nos. | 340
| Installation | Nos. | 340
20.6 | Two way light point for staircase
| Supply | Nos. | 256
| Installation | Nos. | 256
20.7 | To Circuit wiring as in item Nos. (A) 1.10 using (2 R x 2.5 Sqmm + 1R x 1.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 20mm dia 2mm thick PVC FRLSconduit as lighting circuit, being recond from the distribution board to first General light control switch circuit, with circuit RYB colour coding.
| Supply | Mtrs. | 10080
| Installation | Mtrs. | 10080
20.8 | To Circuit wiring as in item Nos. (A) 1.10 using (2 R x 1.5 Sqmm + 1R x 1.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 20mm dia 2mm thick PVC FRLSconduit as lighting circuit, being recond from the distribution board to first Emergency lighting control switch circuit, with circuit RYB colour coding.
| Supply | Mtrs. | 4700
| Installation | Mtrs. | 4700
20.9 | To Circuit wiring as in item Nos. (A) 1.10 using (2 R x 2.5 Sqmm + 1R x 1.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 20mm dia 2mm thick PVC FRLSconduit as lighting circuit, being recond from the distribution board to UPS socket circuit, with circuit RYB colour coding. (UPS power circuit)
| Supply | Mtrs. | 4400
| Installation | Mtrs. | 4400
20.10. | To Circuit wiring as in item Nos. (A) 1.10 using (2 R x 2.5 Sqmm + 1R x 1.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 20/25mm dia 2mm thick PVC FRLSconduit as lighting circuit, being recond from the distribution board to raw power socket circuit, with circuit RYB colour coding. (Raw Power circuit)(Cost include conduit & accessories)
| Supply | Mtrs. | 18032
| Installation | Mtrs. | 18032
20.11 | Sub Main Pantry DB (4 R x 6 Sqmm + 1R x 2.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 32mm dia 2mm thick PVC FRLSconduit as lSb main circuit, being recond from FLoor DB board to Pantry raw power DB, with circuit RYB colour coding. (Raw Power circuit)(Cost include conduit & accessories)
| Supply | Mtrs. | 700
| Installation | Mtrs. | 700
20.12 | To Circuit wiring as in item Nos. (A) 1.10 using (2 R x4 Sqmm + 1R x 2.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 25mm dia 2mm thick PVC FRLSconduit as lighting circuit, being recond from the distribution board to raw power socket circuit, with circuit RYB colour coding. (Raw Power circuit- Dryer)(Cost include conduit & accessories)
| Supply | Mtrs. | 6720
| Installation | Mtrs. | 6720
( B) | Switch & Socket
21.1 | Supply and installation of 1no. Of 6/16 amps 3/5 pin modular type socket controlled by 1no. Of 16 amps SP switch with 3module GI box and accessories etc., (Raw power points for water cooler)
| Supply | Nos. | 112
| Installation | Nos. | 112
21.2 | Supply and installation of 1no. Of 6A amps 3/5 pinsocket controlled by 1no. Of 6 amps SP switch with 3module GI box and accessories etc., (Raw power points in Utility)
| Supply | Nos. | 204
| Installation | Nos. | 204
21.3 | Supply and installation of 1no. Of 6/16 amps 3/5 pin modular type socket controlled by 1no. Of 16 amps SP switch with 3module GI box and accessories etc., (Raw power points)
| Supply | Nos. | 460
| Installation | Nos. | 460
21.4 | Supply and installation of 1no. Of 6A amps 3/5 pin intel socket with out switch and with 2module GI box and accessories etc., (Raw power points for FCU/Elec rm)
| Supply | Nos. | 16
| Installation | Nos. | 16
21.5 | Supply & installation of A/c point. with one no. of 6A 3/5 Pin Socket in Appropriate factory made GI Box, without Switch control and with Wiring by using 2R X 1.5Sqmm + 1R x 1Sqmm PVC insulated FRLS drawn 1100V Grade Multistrand Copper Wire in 20mm dia 2mm thick PVC FRLS conduit of approved make including all conduit accessories. {5 meters}
| Supply | Nos. | 24
| Installation | Nos. | 24
21.6 | Supply and installation of 1no. Of 6A amps 3/5 pin socket with out switch and with 2module GI box and accessories etc., (UPS power points for camera & Wifi)
| Supply | Nos. | 20
| Installation | Nos. | 20
21.7 | Supply and installation of 1no. Of 6A amps 3/5 pin6/16 socket controlled by 1no. Of 6 amps SP switch with 3module GI box and accessories etc., (UPS power points in Utility)
| Supply | Nos. | 32
| Installation | Nos. | 32
21.8 | Supply and installation of 1no. Of 16 amps 3 pin modular type socket with 2m box and controlled by 1no. Of 16 amps SP switch with 1module GI box and accessories etc- Geyser point., (Geyser point )
| Supply | Nos. | 256
| Installation | Nos. | 256
21.9 | To Circuit wiring as in item Nos. (A) 1.10 using (2 R x4 Sqmm + 1R x 2.5Sqmm) sqmm PVC 'insulated FRLS copper wire drawn in 25mm dia 2mm thick PVC FRLSconduit as lighting circuit, being recond from the distribution board to raw power socket circuit, with circuit RYB colour coding. (Raw Power circuit- Geyser)(Cost include conduit & accessories)
| Supply | Mtrs. | 7840
| Installation | Mtrs. | 7840
21.10. | Supply and installation of 2nos. Of 6A amps 3/5 pin socket controlled by 1no. Of 6 amps SP switch with 3module GI box and accessories etc., (UPS power points in Utility)
| Supply | Nos. | 32
| Installation | Nos. | 32
21.11 | Supply & Installation suitable 1/2 module GI box with dummy cover plate for Camera /tv Wifi and service room points
| Supply | Nos. | 40
| Installation | Nos. | 40
21.12 | Supply & Installation suitable 1/2 module GI box for RJ-45 jack outlet points
| Supply | Nos. | 2044
| Installation | Nos. | 2044
21.13 | Supply & Installation of 32mm dia 2mm thick PVC FRLS conduit (excluding wiring) with clamps, bends, suspensions, junction box etc. For data & Wifi outlets
| Supply | Mtrs. | 400
| Installation | Mtrs. | 400
21.14 | Supply & Installation of 25mm dia 2mm thick PVC FRLS conduit (excluding wiring) with clamps, bends, suspensions, junction box etc. For data & Wifi outlets
| Supply | Mtrs. | 16720
| Installation | Mtrs. | 16720
21.15 | Supply & Installation of 20mm dia 2mm thick PVC FRLS conduit (excluding wiring) with clamps, bends, suspensions, junction box etc. data
| Supply | Mtrs. | 19600
| Installation | Mtrs. | 19600
21.16 | Supply & Installation of 25mm dia PVC flexible conduit
| Supply | Mtrs. | 2400
| Installation | Mtrs. | 2400
21.17 | Supply & Installation of 32mm dia 2mm thick PVC FRLS conduit (excluding wiring) with clamps, bends, suspensions, junction box etc. For Power
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
21.18 | Supply & Installation of 25mm dia 2mm thick PVC FRLS conduit (excluding wiring) with clamps, bends, suspensions, junction box etc. For Power
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
21.19 | Supply & Installation of 20mm dia 2mm thick PVC FRLS conduit (excluding wiring) with clamps, bends, suspensions, junction box etc. For lighting
| Supply | Mtrs. | 14780
| Installation | Mtrs. | 14780
TOTAL PART - D
PART - E : LIFT WIRING SYSTEM
22.1 | 3ø, 4Way, ETPN DB (Lift)( as per Vendor Requirement)
Incomers 1No. 63A, 4P, MCB 'C' Curve
Outgoing 1No.63A, 4P, RCCB 'C'300mA
Subincomer 1No. 25A, 2P, 30mA RCCB
Outgoing 1no. Of 25A, DP, MCB 'C' curve
Outgoing 2nos. Of 20A, DP, MCB 'C' curve
| Supply | Nos. | 12
| Installation | Nos. | 12
22.2 | Supply & Installation of Lift way Light point & all shafts with
(2 R X 2.5+1R X1.5)Sqmm FRLS wiring in 20mm dia conduit installed in hoist way .
along with 6A/16A 5 Pin Socket Controlled with Gang box Complete
| Supply | Nos. | 108
| Installation | Nos. | 108
22.3 | Supply & Fixing in lift way with 10W LED Bulkhead fixture ORIENT MAKE
| Supply | Nos. | 108
| Installation | Nos. | 108
22.4 | Supply & Installation of 2R X 4 sq mm Flex. Cable+ 1R x 2.5 Sqmm Flex. Cable in 25mm PVC Conduit lift power point
| Supply | Mtrs. | 400
| Installation | Mtrs. | 400
22.5 | Supply & Installation of 2R X 2.5 sq mm Flex. Cable+ 1R x 1.5 Sqmm Flex. Cable in 20mm PVC Conduit lift Lighting point
| Supply | Mtrs. | 400
| Installation | Mtrs. | 400
22.6 | Supply and installation of 1no. Of 6/16 amps 3/5 pin socket controlled by 1no. Of 16 amps SP switch with 3module GI box and accessories etc., (Lift Well socket)
| Supply | Mtrs. | 108
| Installation | Mtrs. | 108
TOTAL PART - E
PART - F: RISING MAIN
23 | Raising main- C& S / Schneider make
23.1 | Raising mains (BBT) 400A, 3P+100%N, Power raising main with 2Rx40x6mm AL Earthstrip's on outside enclosure
3Phase 4wire Air Insulated 400A Raising Mains with Al Busbars, 3P+ 100% rated neutral, Earth Bus, IP52 in construction, Tap off provision at every 500mm interval complete & necessay supports at regular interval
| Supply | Mtrs | 84
| Installation | Mtrs | 84
24 | End covers
24.1 | End cover plate for 400A raising main
| Supply | Nos. | 8
| Installation | Nos. | 8
25 | End feed unit
25.1 | LTG+RP+AHU raising main end feed unit consisting of 400A, TPN, MCCB with O/L, S/C releases and Shunt trip coil (Maximum Height 1.6mtrs)
| Supply | Nos. | 4
| Installation | Nos. | 4
26 | TAP OFF BOXES
26.1 | Tap off boxes consisting of 1 no 100, 4P, MCCB 25KA, in a proper enclosure for RP (G+6 Floor DB)( 7+2)
| Supply | Nos. | 36
| Installation | Nos. | 36
26.2 | Tap off boxes consisting of 63A, 4P, MCCB 25KA , in a proper enclosure
| Supply | Nos. | RO
| Installation | Nos. | RO
26.3 | Tap off boxes consisting of 160A, 4P, MCCB 25KA , in a proper enclosure
| Supply | Nos. | 4
| Installation | Nos. | 4
* Note : | Kindly note cost of raising mains shall include necessary support system.
TOTAL PART - F
PART - G : EARTHING SYSTEM
26.1 | Supply and installation of earth electrode as per approval of EB :-
Supply and installation of (Copper plate) earth electrode as per approval of EB and the earth electrodes shall be 50mm dia 3000mm long GI pipe confirming to IS 1249, the entire earth installation shall be as per Indian STD code of practice IS 3043 with copper Plate 600 x 600 x 3.15mm (With bolts & nuts) and funnel 'arrangement without cover plate and Civil Works, GI Strip and alternate layers of salt and charcoal.
| Supply | Nos. | 48
| Installation | Nos. | 48
26.2 | Supply and installation of (GI plate) earth electrode as per approval of EB and the earth electrodes shall be 50mm dia 3000mm long GI pipe confirming to IS 1249, the entire earth installation shall be as per Indian STD code of practice IS 3043 with G.I. Plate 600 x 600 x 6mm (With bolts & nuts) and funnel 'arrangement without cover plate and Civil Works, GI Strip and alternate layers of salt and charcoal.
| Supply | Nos. | RO
| Installation | Nos. | RO
26.3 | Supply and made of RCC precast chamber. The concrete inspection pit (Green colour)is load rated to 5000 -10000 kg and is suitable for most types of Earthing and Lightning protection installations.Weight: 110kgA: 450 mm dia with Lid having hook option.
| Supply | Nos. | 48
| Installation | Nos. | 48
26.4 | Supply & Installation of 50 X 6 mm GI Earth Strip
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
26.5 | Supply & Installation of 40 X 6 mm GI Earth Strip
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
26.6 | Supply & Installation of 25 X 6mm Cu Earth Strip
| Supply | Mtrs. | 400
| Installation | Mtrs. | 400
26.7 | Supply & Installation of 8 SWG GI Wire
| Supply | Mtrs. | 1200
| Installation | Mtrs. | 1200
26.8 | Supply & Installation of 25 X 3 mm Copper Earth Strip with required sleeves and insulators at regular interval of 750mm.
| Supply | Mtrs. | 900
| Installation | Mtrs. | 900
26.9 | Supply & Installation of 1C X 70 sq mm Cu Flexible Cable with copper lugs for termination.
| Supply | Mtrs. | 800
| Installation | Mtrs. | 800
26.10. | Supply & Installation of 25 X3 mm Al Earth Flat with proper joint rivit- for Lift
| Supply | Mtrs. | 1600
| Installation | Mtrs. | 1600
Earthing Cable
27 | Supply & Installation of 1C X 4 sq mm Cu Flexible Cable with copper lugs for termination.
| Supply | Mtrs. | 1200
| Installation | Mtrs. | 1200
TOTAL PART - G
PART - H : MISCELLANEOUS
28.1 | Supply & Installation of of Electromat nominal 2.0 mm thick x 1MTR width class A Voltage up to 3.3 KV electrically insulated PVC Synthetic mat confirming to IS:15652:2006 having minimum dielectric strength of 30kv Colour Blue (Fire Retarted)
| Supply & Installation | Sq Mtrs | 160
28.2 | Supply & Installation of 1000mm Wide rubber matting of 11kV grade as per EB rule.
| Supply & Installation | RMtrs. | RO
28.3 | Shock treatment chart as approved by Electrical board and framed and hunged in a pre-dominent position. | Nos. | 28
28.3 | Danger board in Local languagesl/English/Hindi/ in Red colour with 440V marks. | Nos. | 28
28.4 | Supply & Installation of fire bukets stand with 4 Nos. of fire buckets in the stand duly filled with sand. The stand shall be fabricated in the approved manner of the appropirate authorities and located outside of Electrical Panel Room | Nos. | 8
28.5 | Display of Electrical inspectrate Approved Drgs | Nos. | 4
28.6 | Wall chasing and refilling with cement mortor for wall conduiting ( 2"x2") with wire mesh( Mivan Structure ) | RMtrs. | 18000
28.7 | Supply and Installation of LED Aviation Lamp with 2Mtr.,32mm Dia G.I. Pipe supports and fixing accessories make : Bajaj | Nos. | 4
28.8 | Supply and Installation of 400 dia NP -2 Hume Pipe - Cable entry
| Supply | Mtrs. | 80
| Installation | Mtrs. | 80
28.9 | Supply and Installation of 300 dia NP -2 Hume Pipe - Cable entry
| Supply | Mtrs. | 120
| Installation | Mtrs. | 120
28.10. | Supply and Installation of 110 dia PVC 6Kg Pipe -OFC Cable entry
| Supply | Mtrs. | 120
| Installation | Mtrs. | 120
28.11 | Preparation of CEIG drawing, preparation of technical documents, obtaining of drawing approval and Commissiong approval including required coordination | Ls | 4
TOTAL PART - H
PART - I : LT PANEL INSTALLATION
Please Note : All panel Bus should be copper only
29.1 | Supply, Receiving, storing, Shifting, installation and commission of Building Main LT panel -1
| Supply | Nos. | 4
| Installation | Nos. | 4
29.2 | Supply, Receiving, storing, Shifting, installation and commission of Building Main LT panel -2
| Supply | Nos. | 4
| Installation | Nos. | 4
29.3 | Supply,Receiving, storing, Shifting, installation and commission of Wall mounted/FLOOR Fire Emergency panel @ GF Electrical Room
| Supply | Nos. | 4
| Installation | Nos. | 4
29.4 | Supply,Receiving, storing, Shifting, installation and commission of Wall mounted/FLOOR POWER floor DB( FROM RM)
| Supply | Nos. | 28
| Installation | Nos. | 28
29.5 | Supply,Receiving, storing, Shifting, installation and commission of out door terrace utility panel
| Supply | Nos. | 4
| Installation | Nos. | 4
29.6 | Supply Receiving, storing, Shifting, installation and commission of Fabricated Emergency lighting(upS)DB
| Supply | Nos. | 4
| Installation | Nos. | 4
29.7 | Supply,Receiving, storing, Shifting, installation and commission of Wall mounted/Lighting AND POWER RM Floor DB - (ROOM)
| Supply | Nos. | 28
| Installation | Nos. | 28
TOTAL PART- I
PART - J : LIGHT FIXTURE INSTALLATION
Note:
1.All the Light fitting body should be Aluminum.
2. All the Led fitting LED driver Harmonics should have less than 10%THD.
3. The vendor/ supplier should specify Lumen/w each light fitting along with quote
4. All the LED fitting LED driver should built in driver.
5. All the LED fitting before procuring get the approval Architect and client.
6. All the Light fittng Warranty should have 5 years form the after handover.
7. All the Driver Voltage rage 230-260V
30.1 | Supply and installation of Orient 20W LED Batten BT9002, Body made of Aluminium and Acrylic Diffuser with CRI>80, 1200X30X35 H mm, color temperature 3000K/4000K/5700K
Make: Orient, Model: Make:ORIENT TASKLINE (Elec Rm,S/W rm )
| Supply | Nos. | 124
| Installation | Nos. | 124
30.2 | Supply and installation of Surface Mounted High Efficiency ORIENT Surface High Efficiency Round Led Downlight, Body made of Aluminium and Opal Diffuser with homogeneous light distribution and without hotspots, System power 15W, 230V with CRI>80, Dia 150mmX80H mm, color temperature 3000K/4000K/5700K hotspots, System power 12W, 230V with CRI>80, Dia- 147mm X60mm, color temperature 4000K
Make: ORIENT, Model: VENUS
| Supply | Nos. | 32
| Installation | Nos. | 32
30.3 | Supply and Installtion of Orient Batten, Body made of Aluminium and Acrylic Diffuser 20W, with CRI>80, 1200X30X35 H mm, color temperature 3000K/4000K/5700K With PIR Sensor
Make: OrientModel: taskline
| Supply | Nos. | 256
| Installation | Nos. | 256
30.4 | Supply and installation of Surface Mounted High Efficiency ORIENT Surface High Efficiency Round Led Downlight, Body made of Aluminium and Opal Diffuser with homogeneous light distribution and without hotspots, System power 15W, with CRI>80, color temperature 3000K/4000K/5700K hotspots, System power 15W, 240-260VV with CRI>80, Dia- 147mm X60mm, color temperature 4000K
Make: ORIENT, Model: VENUS
| Supply | Nos. | 1084
| Installation | Nos. | 1084
30.5 | Supply and installation of Hi-efficiency LED Linear Flood Luminaire,ORIENT , LEDLuminaire, Body made of di-cast aluminium and hi-precision optics with beam angles 90º/120º System power 80W, 230V, CRI>70, Dia 270 X254H mm, color temperature 3000K/4000K/5700K with IP65
Make: ORIENT, Model: SIGMA PC UHL
| Supply | Nos. | 12
| Installation | Nos. | 12
30.6 | Supply and installation of recess mounted high efficiency LED round down light Body made of Aluminium and Opal Diffuser with homogeneous light distribution and without hotspots, System power 18W, 230-260V with CRI>80, Dia- 152mm X61mm, color temperature
Make:Orient Model Dazzler
| Supply | Nos. | RO
| Installation | Nos. | RO
30.7 | Supply and installation of Orient Deep Recessed High Efficiency Round Led Downlight, Body made of Aluminium Diecast and Opal Diffuser with homogeneous light distribution and without hotspots, System power 10W, 230V with CRI>80, Dia 120X50 H mm, Cut Out Dia 110mm color temperature 3000K/4000K/5700K hotspots, System power 10W, 230V with CRI>80, Dia- 119mm X58mm, color temperature Model - Dazzler
Make:Orient Model Dazzler
| Supply | Nos. | 488
| Installation | Nos. | 488
30.8 | Supply and installation of 10W LED type bulk head lamp
orient make Hi-efficiency LED Bulkhead Luminaire, Body made of di-cast aluminium housing , System power 12W, 150V -270V, CRI>80, 212 mm X 82 X 70H mm , color temperature 5700K. With mounting accessories, IP65
| Supply | Nos. | 24
| Installation | Nos. | 24
30.8 | Supply and installation 1 * 56 watts 1200MM Sweep, 320RPM, 220CMM 3 Blade Ceiling Fan. Note: should work with regulator.(Reception & OTHER AREA)
Make: Orient , Model: NEW BREEZE BODY COLOUR WHITE
| Supply | Nos. | 76
| Installation | Nos. | 76
30.9 | Supply and installation 1 * 38, watts 900MM Sweep 3 Blade, 400RPM, 140CMM AIR DELIVER Ceiling Fan. Note: should work with regulator.(pantry & OTHER AREA)
Make: Orient , Model: NEW BREEZE BODY COLOUR WHITE
| Supply | Nos. | 80
| Installation | Nos. | 80
30.10. | Supply and installation of ORIENT Deep Recessed High Efficiency Round Led Downlight, Body made of Aluminium Diecast and Opal Diffuser with homogeneous light distribution and without hotspots, System power 15W, 230V with CRI>80, Dia Cut Out Dia 145mm color temperature 3000K/4000K/5700K hotspots, System power 15W, 230V with CRI>80, Dia-152mm X61mm, color temperature
Make: ORIENT, Model: DAZZLER
| Supply | Nos. | 416
| Installation | Nos. | 416
30.11 | Supply and Installtion Surface Mounted High Efficiency Round Led Downlight, Body made of Aluminium and Opal Diffuser with homogeneous light distribution and without hotspots, System power 18W, 180-260V with CRI>80, Dia 100X165H mm, color temperature 3000K/4000K/5700K IP65 free glass with neoprene rubber gasket with out door fixing bracket and accessories dimension 96mm dia x135mm H - Canopy Philips /Eq
| Supply | Nos. | 48
| Installation | Nos. | 48
30.12 | 4 feet -ORIENT MAKE High Efficiency Suspended LED Channel, Body made of Aluminium and PMMA Diffuser with homogeneous light distribution and without hotspots, System power 36W, 230V, 1800mm X 70mm X 85mm, Color Temperature 4000K/5700 LCPDL6-48-C-70
| Supply | Nos. | RO
| Installation | Nos. | RO
30.13 | Supply and Installation of Orient LED Batten , Body made of Aluminium and Acrylic Diffuser 20W, with CRI>80, 1200X30X35 H mm, color temperature 3000K/4000K/5700K Model-Taskline SQ
| Supply | Nos. | 116
| Installation | Nos. | 116
30.14 | Supply and installation of Orient Deep Recessed High Efficiency Round Led Downlight, Body made of Aluminium Diecast and Opal Diffuser with homogeneous light distribution and without hotspots, System power 18W, 240-260V with CRI>80, Dia 155X58 H mm, Cut Out Dia 145mm color temperature 3000K/4000K/5700K hotspots, System power 18W, 230V with CRI>80, Dia- 1152mm X61mm, color temperature
Make: Orient, Model: Dazzler
| Supply | Nos. | 88
| Installation | Nos. | 88
30.15 | Supply and Installtion of Exhaust Fan orient make 294x262 mm Ventilator DX Ventilator DX 250mm (9.84 inch) Exhaust Fan for Toilet - toilet, wasing area etc
| Supply | Nos. | 340
| Installation | Nos. | 340
TOTAL PART - J
GRAND TOTAL (IIIA)
(IIIB) | ELECTRICAL WORKS (KITCHEN & CAFATERIA))
PART 'A' - INTERNAL CABLE WORK
31 | Supply, Installation, Testing & Commissioning of 1100V grade, Aluminum / copper conductor, PVC / XLPE Insulated & galvainsed steel tape armouring .The cable shall be heavy duty type conforming to IS-1554 & 7098. The cable shall be suitable to lay directly underground in Existing trenches/ RCC Ducts/Sleeves/ Cable trays. Rate shall be excluding of cabling laying related civil work.
(A) | Aluminium Armoured XLPE Insulated cables
31.1 | Supply & Installation of 3.5C X 240 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
31.2 | Supply & Installation of 3.5C X 185 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 60
| Installation | Mtrs. | 60
31.3 | Supply & Installation of 3.5C X 35 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 15
| Installation | Mtrs. | 15
31.4 | Supply & Installation of 4C X 25 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 100
| Installation | Mtrs. | 100
31.5 | Supply & Installation of 4C X 16 Sq mm Aluminum Armoured cables
| Supply | Mtrs. | 100
| Installation | Mtrs. | 100
(B) | Copper Armoured XLPE/PVC Insulated cables
32.1 | Supply & Installation of 4C X 35 Sq mm Copper Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
32.2 | Supply & Installation of 4C X 25 Sq mm Copper Armoured cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
32.3 | Supply & Installation of 4C X 16 Sq mm Copper Armoured cables
| Supply | Mtrs. | 394
| Installation | Mtrs. | 394
32.4 | Supply & Installation of 4C X 10 Sq mm Copper armoured cable
| Supply | Mtrs. | 20
| Installation | Mtrs. | 20
32.5 | Supply & Installation of 4C X 6 Sq mm Copper armoured cable
| Supply | Mtrs. | 188
| Installation | Mtrs. | 188
32.6 | Supply & Installation of 4C X 4 Sq mm Copper armoured cable
| Supply | Mtrs. | 209
| Installation | Mtrs. | 209
32.7 | Supply & Installation of 4C X 2.5 Sq mm Copper armoured cable
| Supply | Mtrs. | 950
| Installation | Mtrs. | 950
(C) | Copper Armoured PVC FRLS Insulated cables
33.1 | Supply & Installation of 4C X 16 Sq mm Copper FRLS Flexible cable cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
33.2 | Supply & Installation of 4C X 10 Sq mm Copper FRLS Flexible cable cables
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
33.3 | Supply & Installation of 4C X 6 Sq mm CopperFRLS Flexible cable cables
| Supply | Mtrs. | 188
| Installation | Mtrs. | 188
33.4 | Supply & Installation of 4C X 4 Sq mm Copper FRLS Flexible cable cables
| Supply | Mtrs. | 1418
| Installation | Mtrs. | 1418
33.5 | Supply & Installation of 4C X 2.5 Sq mm Copper FRLS Flexible cable cables
| Supply | Mtrs. | 80
| Installation | Mtrs. | 80
D | End terminations & Gland Earthing
Note:
1. Single compression brass gland should be provided for all type of multi core armoured cables of size below 95 Sq. mm.
2. Double compression brass gland should be provided for all type of multi core armoured cables of size including 95sqmm and above
3. PVC gland should be provided for single core & multi core flexible copper cables
4. Only copper lugs should be used for aluminum and copper armoured / unarmoured cables irrespective of sizes
(A) | Aluminium Armoured XLPE Insulated cable termination with copper lugs
34.1 | Supply & Installation of 3.5C X 240 Sq mm Aluminum Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
34.2 | Supply & Installation of 3.5C X 185 Sq mm Aluminum Armoured cables
| Supply | Nos. | 4
| Installation | Nos. | 4
34.3 | Supply & Installation of 3.5C X 35 Sq mm Aluminum Armoured cables
| Supply | Nos. | 2
| Installation | Nos. | 2
34.4 | Supply & Installation of 4C X 25 Sq mm Aluminum Armoured cables
| Supply | Nos. | 6
| Installation | Nos. | 6
34.5 | Supply & Installation of 4C X 16 Sq mm Aluminum Armoured cables
| Supply | Nos. | 4
| Installation | Nos. | 4
(B) | Copper Armoured XLPE/PVC Insulated cables
35.1 | Supply & Installation of 4C X 35 Sq mm Copper Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
35.2 | Supply & Installation of 4C X 25 Sq mm Copper Armoured cables
| Supply | Nos. | RO
| Installation | Nos. | RO
35.3 | Supply & Installation of 4C X 16 Sq mm Copper Armoured cables
| Supply | Nos. | 20
| Installation | Nos. | 20
35.4 | Supply & Installation of 4C X 10 Sq mm Copper armoured cable
| Supply | Nos. | 4
| Installation | Nos. | 4
35.5 | Supply & Installation of 4C X 6 Sq mm Copper armoured cable
| Supply | Nos. | 12
| Installation | Nos. | 12
35.6 | Supply & Installation of 4C X 4 Sq mm Copper armoured cable
| Supply | Nos. | 209
| Installation | Nos. | 209
35.7 | Supply & Installation of 4C X 2.5 Sq mm Copper armoured cable
| Supply | Nos. | 44
| Installation | Nos. | 44
(D) | Copper Armoured PVC FRLS Insulated cables
36.1 | Supply & Installation of 4C X 16 Sq mm Copper FRLS Flexible cable cables
| Supply | Nos. | RO
| Installation | Nos. | RO
36.2 | Supply & Installation of 4C X 10 Sq mm Copper FRLS Flexible cable cables
| Supply | Nos. | RO
| Installation | Nos. | RO
36.3 | Supply & Installation of 4C X 6 Sq mm CopperFRLS Flexible cable cables
| Supply | Nos. | 4
| Installation | Nos. | 4
36.4 | Supply & Installation of 4C X 4 Sq mm Copper FRLS Flexible cable cables
| Supply | Nos. | 68
| Installation | Nos. | 68
36.5 | Supply & Installation of 4C X 2.5 Sq mm Copper FRLS Flexible cable cables
| Supply | Nos. | 4
| Installation | Nos. | 4
E | CABLE TRAY
Supply & Installation of Factory made GI sheet metal type cable trays made out of 2/1.6mm thick . The cable tray shall be supplied as specified with necessary supports, all accessories like bend, Tees etc manufactured at the manufacturers work as per Drawing and required at site condition. The tray should be provided with adequate supports, the distance supports shall not be more than 1.2 to 1.5 meter . Coupler plate & galvanized hardware should be used to join the cable tray section. Earthing continuity shall be ensured at each joint. Cost to include rate of ceiling supports also. (Cable trays should be bolted type)
( A ) | GI Perforated type/Raceway
37.1 | 600mm wide with 75 mm depth 2 mm thick ceiling raceway
| Supply | Mtrs. | 42
| Installation | Mtrs. | 42
37.2 | 450mm wide with 75 mm depth 2 mm thick ceiling raceway with Cover
| Supply | Mtrs. | 19
| Installation | Mtrs. | 19
37.3 | 300mm wide with 75 mm depth 2 mm thick ceiling raceway with Cover
| Supply | Mtrs. | 17
| Installation | Mtrs. | 17
37.4 | 150mm wide with 75 mm depth 2 mm thick ceiling raceway with Cover
| Supply | Mtrs. | 40
| Installation | Mtrs. | 40
37.5 | 600mm wide with 75 mm depth 2 mm thick Ladder type cable trays
| Supply | Mtrs. | 40
| Installation | Mtrs. | 40
37.6 | 300mm wide with 75 mm depth 2 mm thick Ladder type cable trays
| Supply | Mtrs. | 20
| Installation | Mtrs. | 20
37.7 | 150 mm wide with 75 mm depth 2 mm thick Ladder type cable trays
| Supply | Mtrs. | 15
| Installation | Mtrs. | 15
37.8 | 150mm wide with 50 mm depth 2 mm thick ceiling raceway with Cover( net working)
| Supply | Mtrs. | 20
| Installation | Mtrs. | 20
TOTAL PART - A
PART - B : DISTRIBUTION BOARDS.
38 | Supply, Installation, Testing and commissioning of Distribution Boards, IP 43 (Double door) As per IS 2675 made out of 16swg GI sheet steel enclosure hinged GI cover/over flanged cover with cutouts for operating the MCB knobs and comprising of phase busbars, neutrals and earth bus with tapped holes, Bakelite phase shall be mounted by grouting in to the wall / angle to brick wall as required. DBs shall be suitable for single / three phase loads, Including fixing angle, DB termination lugs, PPI kits etc.
(Notes: Local fabrication Not permitted. Only factory made boxes shall be installed)
LIGHTING DB
38.1 | 3ø, 8Way, ETPN DB
Incomers 1No. 25A, 4P, 10kA,MCB 'C' Curve
Phase outgoing 3Nos. 25A, 30mA, DP, RCCB
18Nos. Of outgoing 10A SP MCB With 'C' Curve
| Supply | Nos. | 2
| Installation | Nos. | 2
RAW POWER DB
38.2 | 3ø, 8Way ETPN DB
Incomers 1No. 63A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 40A, 30mA, DP, RCCB
17Nos. Of outgoing 16A SP MCB With 'C' Curve
1No. Of outgoing 20A SP MCB With 'C' Curve
| Supply | Nos. | 3
| Installation | Nos. | 3
38.3 | 3ø, 6Way ETPN DB
Incomers 1No. 63A, 4P, MCB 'C' Curve
Phase outgoing 3Nos. 40A, 30mA, DP, RCCB
16Nos. Of outgoing 16A SP MCB With 'C' Curve
2Nos. Of outgoing 20A SP MCB With 'C' Curve
| Supply | Nos. | 1
| Installation | Nos. | 1
38.4 | 1ø,8Way, SPN DB ( emergency Lighting )
incomers 1No. 25A, DP, RCCB '30 mA
6Nos. Of outgoing 6A SP MCB With 'C' Curve
| Supply | Nos. | 2
| Installation | Nos. | 2
38.5 | 3ø, 4Way ETPN DB ( UPS out put DB)
Incomers 1N40A, 4P, MCB 'D' Curve
3Nos. Of outgoing 25A DP MCB With 'D' Curve
1Nos. Of 15KVA surge suresser
| Supply | Nos. | 1
| Installation | Nos. | 1
38.6 | 1ø,8Way, SPN DB (UPS)
Incomers 1No. 25A, DP, MCB
6Nos. Of outgoing 10/16A SP MCB With 'D' Curve
| Supply | Nos. | 1
| Installation | Nos. | 1
38.7 | 12Way, SPN DB- Bain-marie DB
Incomers 1No. 32A, 4P, MCB 'C' Curve
Phase outgoing 4Nos. 25A, 30mA, DP, RCCB
| Supply | Nos. | 4
| Installation | Nos. | 4
38.8 | Supply and Installation of IP 65 Industrial Suitable Plug and socket Make Legrand Single Phase 16/20 2p+E with 25A 100mA DP RCCB Socket Model- 056661
| Supply | Nos. | 10
| Installation | Nos. | 10
38.9 | Supply and Installation of IP 65 Industrial Suitable Plug and socket Make Legrand 1 Phase 32 2p+E with 4P 25A 100mA RCCB Socket Model - 056669
| Supply | Nos. | 4
| Installation | Nos. | 4
38.10. | Supply and Installation of IP 65 Industrial SuitablePlug and socket Make Legrand 3 Phase 32 3P+N+E with4P 25A 100mA RCCB - Socket Model 056673
| Supply | Nos. | 74
| Installation | Nos. | 74
38.11 | Supply and Installation of IP 65 Industrial SuitablePlug and socket Make Legrand 3 Phase 32 3P+N+E with 4P 40A 100mA RCCB Socket Model- 056674
| Supply | Nos. | 10
| Installation | Nos. | 10
38.12 | Supply and Installation of IP 65 Industrial SuitablePlug and socket Make Legrand 3 Phase 63 3P+N+E with 4P 40A 100mA RCCB Socket Model- 056674
| Supply | Nos. | 4
| Installation | Nos. | 4
38.13 | Supply and Installation of IP 65 Industrial Suitable Plug and socket Make Legrand 3 Phase 63A 3P+N+E with 4P63A MCB Socket Model - 056674
| Supply | Nos. | 2
| Installation | Nos. | 2
38.14 | Supply and Installation IP 65 enclosure with 63A/8 4P MCCB with door Handle - Make Hensal/Schneider.- Dish wash
| Supply | Nos. | 4
| Installation | Nos. | 4
38.15 | Supply and Installation of DOL starter up to 3.7 KW
| Supply | Nos. | 16
| Installation | Nos. | 16
38.16 | Supply and Installation of single phase Mobile Plug and socket Make -Legrand Model 5555 24 Socket -5555 04
| Supply | Nos. | 12
| Installation | Nos. | 12
38.17 | Supply and Installation Legrand make IP 65 plxo box enclosure with 40A 4 Pole MCB
| Supply | Nos. | 4
| Installation | Nos. | 4
TOTAL OF PART - B
PART - C : INTERNAL WIRING
A | Supply & Installation, Testing and Commissioning of point wiring using 2 x 1.5 + 1 R x 1.0 sqmm PVC insulated FRLS multi stranded 1100V grade copper wires drawn in 20mm dia 2mm thick PVC FRLS conduit including all conduit accessories such as bends, Junction boxes etc. The wiring shall be done in complete looping in system. The switches used shall be moulded on ORIENT MAKE MODULE SALUS GREY COLOUR integral GI box with clear earthing facility. The wiring shall be complete with ceiling, switches and all consumables, connectors etc., The lighting circuit number to be placed in switch plate with sticker and ferrules . (Colour coding of wiring should be adopted)- Dining area
39.1 | One light point controlled by one switch considered as primary point. (4 mtr Single Height area) {18 meters}
| Supply | Nos. | 120
| Installation | Nos. | 120
39.2 | For every additional secondary point. ( 4Mtr Single height) {6meters} (General Lighting)
| Supply | Nos. | 230
| Installation | Nos. | 230
39.3 | Wall mounted fan point socket near fan 2.5mtr switch at 1200mm 10/6A one way switch regulator. {8 meters}- 4mtr height
| Supply | Nos. | 8
| Installation | Nos. | 8
39.4 | One light point controlled by one switch considered as primary point. (8 mtr Double Height area) {20 meters}
| Supply | Nos. | 4
| Installation | Nos. | 4
39.5 | For every additional secondary point. (8 Mtr Double height) {5meters} (General Lighting)
| Supply | Nos. | 4
| Installation | Nos. | 4
39.6 | One Fan controlled by One no of One way switch with step type electronic regulator. {18 meters}- 4mtr height
| Supply | Nos. | 51
| Installation | Nos. | 51
39.7 | exhaust fan point controlled by one switch near door along with socket considered as . (Single Height area)- 4 mtr height {15meters}
| Supply | Nos. | 3
| Installation | Nos. | 3
39.8 | Light points for staircase.(two way ), 3/2 lights consider cost of 2 module box with wiring
| Supply | Nos. | 12
| Installation | Nos. | 12
B | Supply & Installation, Testing and Commissioning of point wiring using 2 x 1.5 + 1 R x 1.0 sqmm PVC insulated FRLS multi stranded 1100V grade copper wires drawn in 25mm 1.6 mm thick GI conduit including all conduit accessories such as bends, Junction boxes etc. The wiring shall be done in complete looping in system. The switches used shall be moulded on Approved Make integral GI box with clear earthing facility. The wiring shall be complete with ceiling, switches and all consumables, connectors etc., The lighting circuit number to be placed in switch plate with sticker and ferrules . (Colour coding of wiring should be adopted)- KITCHEN AREA
40.1 | One light point controlled by one switch considered as primary point. (4 mtr Height area) {15 meters}
| Supply | Nos. | 50
| Installation | Nos. | 50
40.2 | For every additional secondary point. ( 4Mtr Single height) {6meters} (General Lighting)
| Supply | Nos. | 75
| Installation | Nos. | 75
40.3 | To Circuit wiring as in item Nos. (A) 1.10 using (2Rx2.5 Sqmm+1R x 1.5Sqmm) sqmm PVC 'insulated copper wire drawn in 20mm dia 2mm thick PVC FRLS conduit/ in perforated cable tray as lighting/power circuit, being recond from the distribution board to first general light, fan & emergency lighting control switch circuit, with circuit RYB colour coding. Dining area(including conduit) dining area
| Supply | Mtrs. | 1200
| Installation | Mtrs. | 1200
40.4 | To Circuit wiring as in item Nos. (A) GI conduit using (2Rx2.5 Sqmm+1R x 1.5Sqmm) sqmm PVC 'insulated copper wire drawn in 20mm dia 2mm thick PVC FRLS conduit/ in perforated cable tray as lighting/power circuit, being recond from the distribution board to first general light, fan & emergency lighting control switch circuit, with circuit RYB colour coding. Dining area( including conduit)
| Supply | Mtrs. | 540
| Installation | Mtrs. | 540
40.5 | Supply & Installation of 25mm dia 2mm thick PVC conduit in floor (excluding wiring) with clamps, bends, suspensions, junction box etc. (power)
| Supply | Mtrs. | 2500
| Installation | Mtrs. | 2500
C | POWER CONDUITS
41.1 | Supply & Installation of 32mm dia 2mm thick GI conduit in ceiling (excluding wiring) with clamps, bends, suspensions, junction box etc. (power)
| Supply | Mtrs. | 430
| Installation | Mtrs. | 430
41.2 | Supply & Installation of 32mm dia 2mm thick GA conduit in ceiling (excluding wiring) with clamps, bends, suspensions, junction box etc. (data)
| Supply | Mtrs. | 70
| Installation | Mtrs. | 70
41.3 | Supply & Installation of 25mm dia 2mm thick GA conduit in floor (excluding wiring) with clamps, bends, suspensions, junction box etc. (power)
| Supply | Mtrs. | 225
| Installation | Mtrs. | 225
D | LIGHTING & FAN CONDUITS
42.1 | Supply & Installation of 25mm dia 2mm thick GA conduit in ceiling (excluding wiring) with clamps, bends, suspensions, junction box etc. FOR LIGHTING CIRCUIT MAIN
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
42.2 | Supply & Installation of 20mm dia 2mm thick GA conduit in ceiling (excluding wiring) with clamps, bends, suspensions, junction box etc. FOR LIGHT POINTS LOOPING
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
42.3 | Supply & Installation of 25mm dia 2mm thick GA conduit in ceiling (excluding wiring) with clamps, bends, suspensions, junction box etc. FOR EMERGENCY LIGHTING CIRCUIT MAIN
| Supply | Mtrs. | 105
| Installation | Mtrs. | 105
42.4 | Supply & Installation of 20mm dia 2mm thick GA conduit in ceiling (excluding wiring) with clamps, bends, suspensions, junction box etc. FOR EMERGENCY LIGHT POINTS LOOPING
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
42.5 | Supply & Installation of 20 mm dia 2mm thick PVC conduit in floor (excluding wiring) with clamps, bends, suspensions, junction box etc. CCTV
| Supply | Mtrs. | 950
| Installation | Mtrs. | 950
42.6 | Supply & Installation of 25mm dia 2mm thick PVC conduit in floor (excluding wiring) with clamps, bends, suspensions, junction box etc. CCTV
| Supply | Mtrs. | 100
| Installation | Mtrs. | 100
42.7 | Supply and Installation of 3Cx2.5 Sqmm FRLS Copper flexible cable for Raw power
| Supply | Mtrs. | 3120
| Installation | Mtrs. | 3120
42.8 | Supply and Installation of 3Cx4 Sqmm FRLS Copper flexible cable for Raw power
| Supply | Mtrs. | 180
| Installation | Mtrs. | 180
D | Switch & Socket
43.1 | 1no. Of 6/16 amps Socket controlled by 1no. Of 16 amps SP switch (Raw Power) Ip 54 Plaxo box for kitchen inside
| Supply | Nos. | 10
| Installation | Nos. | 10
43.2 | 1no. Of 6/16 amps Socket controlled by 1no. Of 16 amps SP switch (Raw Power)
| Supply | Nos. | 34
| Installation | Nos. | 34
43.3 | 1no. Of 6 amps Socket controlled by 1no. Of 6 amps SP switch (Raw Power)
| Supply | Nos. | 107
| Installation | Nos. | 107
TOTAL PART - C
PART -D : Supply and Installation of Light Fitting
Supply ,Installation of light fitting including necessary consumables. The LED light fitting driver should less than 10% THD,Driver Voltage range 180-260V, Warranty 5 years. - Before supplying of light fitting vendor should submit the TDS,Sample for Architect /consultant and Client approval
44.1 | Supply andInstalltion 4 feet 36/40W Linear suspended/ surface mounted IP65 weather proof light fixture- kitchen ORIENT MAKE IP65 model no STARLINE SLEEK(BATTEN IP65) - Kitchen
| Supply | Nos. | 124
| Installation | Nos. | 124
44.2 | Supply andInstalltion 4 feet 40W Surface mounted al body with diffuser light fixture dinning area. Make -ORIENT model STARLINE Dining area
| Supply | Nos. | 114
| Installation | Nos. | 114
44.3 | Supply and Installation of 20W LED Batten TASKLINE, Body made of Aluminium and Acrylic Diffuser 20W, with CRI>80, 1200X30X35 H mm, color temperature 3000K/4000K/5700K With PIR Sensor
Make: ORIENT, Model: TASKLINE
| Supply | Nos. | 28
| Installation | Nos. | 28
44.4 | Supply and Installation of 80 watts aluminium die cast housing having heat dissipating fins for larger surface area with Polycarbonate integrated lens in the front of LEDs. Available in 60° & 90° beam angles.Powered by an independent electronic LED driver (SMPS based constant current supply) with Output Short-circuit protection, Surge protection & other reliability tests satin finish powder coating.. VERTEX SPIRAL ONE Make :ORIENT Model HI BAY LIGHT
| Supply | Nos. | 8
| Installation | Nos. | 8
44.5 | Supply and installation 1 * 56 watts 1200MM Sweep, 320rpm,220CMM. 3 Blade Ceiling Fan. Note: should work with regulator.(dining area)
Make: Orient , Model: New BREEZE -WHITE
| Supply | Nos. | 51
| Installation | Nos. | 51
44.6 | Supply and installation 1 * 56 watts 1400MM Sweep, 300rpm,255CMM. 3 Blade Ceiling Fan. Note: should work with regulator.(dining area)
Make: Orient , Model: New BREEZE -WHITE
| Supply | Nos. | RO
| Installation | Nos. | RO
44.7 | Supply and Installation of ORIENT LED Batten , Body made of Aluminium and Acrylic Diffuser 20W, with CRI>80, 1200X30X35 H mm, color temperature 3000K/4000K/5700K ELECTRICAL ROOM MODEL -TASK LINE
| Supply | Nos. | 8
| Installation | Nos. | 8
44.8 | Supply and installation of ORIENT Deep Recessed High Efficiency Round Led Downlight, Body made of Aluminium Diecast and Opal Diffuser with homogeneous light distribution and without hotspots, System power 18W, 180-260V with CRI>80, Dia 155X58 H mm, Cut Out Dia 143mm color temperature 3000K/4000K/5700K hotspots, System power 18W, 230V with CRI>80, Dia- 152mm X61mm, color temperature Dining Washing area
Make: ORIENT, Model: DAZZLER
| Supply | Nos. | 40
| Installation | Nos. | 40
44.9 | Supply and installation of ORIENT Deep Recessed High Efficiency Round Led Downlight, Body made of Aluminium Diecast and Opal Diffuser with homogeneous light distribution and without hotspots, System power 15W, 180-260V with CRI>80, Dia 155X58 H mm, Cut Out Dia 145mm color temperature 3000K/4000K/5700K hotspots, System power 15W, 230V with CRI>80, Dia- 152mm X61mm, color temperature- Kitchen rest room
Make: ORIENT Model: DAZZLER
| Supply | Nos. | 12
| Installation | Nos. | 12
44.10. | Supply and Installation of wall mounted 450mm sweep ,1325 RPM Fan Make ORIENT ModelTORNADO-II WALL
| Supply | Nos. | 8
| Installation | Nos. | 8
44.11 | Supply and Installation of wall mounted 300mm exhaust Fan Make ORIENT 1300 RPM ,1290 CMH Model: HIGH AIR WITH BIRD GUARD
| Supply | Nos. | 2
| Installation | Nos. | 2
Total Part- D
PART - E : LIFT WIRING SYSTEM
45.1 | 3ø, 4Way, ETPN DB (Lift)( as per Vendor Requirement)
Incomers 1No. 63A, 4P, MCB 'C' Curve
Outgoing 1No.63A, 4P, RCCB 'C'300mA
Sub incomer 1No. 25A, 2P, 30mA RCCB
Outgoing 1no. Of 25A, DP, MCB 'C' curve
Outgoing 2nos. Of 20A, DP, MCB 'C' curve
| Supply | Nos. | 1
| Installation | Nos. | 1
45.2 | Supply & Installation of Lift way Light point & all shafts with
(2 R X 2.5+1R X1.5)Sqmm FRLS wiring in 20mm dia conduit installed in hoist way .
along with 6A/16A 5 Pin Socket Controlled with Gang box Complete
| Supply | Nos. | 4
| Installation | Nos. | 4
45.3 | Supply & Fixing in lift way with 10W LED Bulkhead fixture orient
| Supply | Nos. | 4
| Installation | Nos. | 4
45.4 | Supply & Installation of 2R X 4 sq mm Flex. Cable+ 1R x 2.5 Sqmm Flex. Cable in 25mm PVC Conduit lift power point
| Supply | Mtrs. | 25
| Installation | Mtrs. | 25
45.5 | Supply & Installation of 2R X 2.5 sq mm Flex. Cable+ 1R x 1.5 Sqmm Flex. Cable in 20mm PVC Conduit lift Lighting point
| Supply | Mtrs. | 25
| Installation | Mtrs. | 25
45.6 | Supply and installation of 1no. Of 6/16 amps 3/5 pin socket controlled by 1no. Of 16 amps SP switch with 3module GI box and accessories etc., (Lift Well socket)
| Supply | Mtrs. | 4
| Installation | Mtrs. | 4
TOTAL PART - E
PART - F : EARTHING SYSTEM
46.1 | Supply and installation of earth electrode as per approval of EB :-
Supply and installation of (Copper plate) earth electrode as per approval of EB and the earth electrodes shall be 50mm dia 3000mm long GI pipe confirming to IS 1249, the entire earth installation shall be as per Indian STD code of practice IS 3043 with copper Plate 600 x 600 x 3.15mm (With bolts & nuts) and funnel 'arrangement without cover plate and Civil Works, GI Strip and alternate layers of salt and charcoal.
| Supply | Nos. | 8
| Installation | Nos. | 8
46.2 | Supply and installation of (GI plate) earth electrode as per approval of EB and the earth electrodes shall be 50mm dia 3000mm long GI pipe confirming to IS 1249, the entire earth installation shall be as per Indian STD code of practice IS 3043 with G.I. Plate 600 x 600 x 6mm (With bolts & nuts) and funnel 'arrangement without cover plate and Civil Works, GI Strip and alternate layers of salt and charcoal.
| Supply | Nos. | RO
| Installation | Nos. | RO
46.3 | Supply and made of RCC precast chamber. The concrete inspection pit (Green colour)is load rated to 5000 -10000 kg and is suitable for most types of Earthing and Lightning protection installations.Weight: 110kgA: 450 mm dia with Lid having hook option.
| Supply | Nos. | 8
| Installation | Nos. | 8
46.4 | Supply & Installation of 50 X 6 mm GI Earth Strip
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
46.5 | Supply & Installation of 40 X 6 mm GI Earth Strip
| Supply | Mtrs. | RO
| Installation | Mtrs. | RO
46.6 | Supply & Installation of 25 X 6mm Cu Earth Strip
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
46.7 | Supply & Installation of 8 SWG GI Wire
| Supply | Mtrs. | 300
| Supply | Mtrs. | 300
46.8 | Supply & Installation of 25 X 3 mm Copper Earth Strip with required sleeves and insulators at regular interval of 750mm.
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
46.9 | Supply & Installation of 1C X 70 sq mm Cu Flexible Cable with copper lugs for termination.
| Supply | Mtrs. | 150
| Installation | Mtrs. | 150
47.1 | Supply & Installation of 25 X3 mm Al Earth Flat with proper joint rivet- for Lift
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
Earthing Cable
47.2 | Supply & Installation of 1C X 4 sq mm Cu Flexible Cable with copper lugs for termination.
| Supply | Mtrs. | 300
| Installation | Mtrs. | 100
47.3 | Supply & Installation of 1C X 2.5 sq mm Cu Flexible Cable with copper lugs for termination.
| Supply | Mtrs. | 1350
| Installation | Mtrs. | 1350
47.4 | Supply & Installation of 1C X 6 sq mm Cu Flexible Cable with copper lugs for termination.
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
TOTAL PART - F
PART - G : MISCELLANEOUS
48.1 | Supply & Installation of Electromat nominal 2.0 mm thick x 1MTR width class A Voltage up to 3.3 KV electrically insulated PVC Synthetic mat confirming to IS:15652:2006 having minimum dielectric strength of 30kv Colour Blue (Fire Retarted)
| Supply & Installation | Sq Mtrs | 20
48.2 | Supply & Installation of 1000mm Wide rubber matting of 11kV grade as per EB rule.
| Supply & Installation | RMtrs. | RO
48.3 | Shock treatment chart as approved by Electrical board and framed and hunged in a pre-dominent position. | Nos. | 2
48.4 | Danger board in Local languagesl/English/Hindi/ in Red colour with 440V marks. | Nos. | 2
48.5 | Supply & Installation of fire buckets stand with 4 Nos. of fire buckets in the stand duly filled with sand. The stand shall be fabricated in the approved manner of the appropriate authorities and located outside of Electrical Panel Room | Nos. | 2
48.6 | Display of Electrical inspectorate Approved Drgs | Nos. | 1
48.7 | Wall chasing and refilling with cement mortor for wall conduiting ( 2"x2") with wire mesh( Mivan Structure ) | RMtrs. | 500
48.8 | Supply and Installation of LED Aviation Lamp with 2Mtr.,32mm Dia G.I. Pipe supports and fixing accessories make : Bajaj | Nos. | 1
48.9 | Supply and Installation of 450 dia NP2 Hume pipe with excavation and back filling
| Supply | Mtrs. | 10
| Installation | Mtrs. | 10
48.10. | Supply and Installation of 300 dia NP2 Hume pipe with excavation and back filling
| Supply | Mtrs. | 10
| Installation | Mtrs. | 10
48.11 | Supply and Installation of 110 dia PVC pipe 6kg with excavation and back filling
| Supply | Mtrs. | 10
| Installation | Mtrs. | 10
48.12 | Preparation of CEIG drawing, preparation of technical documents, obtaining of drawing approval and Commissiong approval including required coordination | Ls | 1
TOTAL PART - G
PART H :LIGHTNING PROTECTION SYSTEM
49 | PART A @ RING EARTHING SYSTEM UNDER SOIL
49.1 | Supply & Installation of 10 mm dia copper bonded Solid Steel Round Conductor with minimum coating thickness 100µm for earthing system. Material should be tested Tensile strength, Electrical Resistance, salt mist, Bend & Adhesion to meet the requirements of IS/ IEC 62305 and IEC 62561-1&2. CAPE Type: SRC10CuB
| Supply | Mtrs. | 200
| Installation | Mtrs. | 200
49.2 | Supply & Installation of Corrosion Bitumen tape for inside soil. CAPE Type: CT5
| Supply | Nos. | 7
| Installation | Nos. | 7
49.3 | Installation of Exothermic Welding - Including welding mould and other accessories for welding confirms the requirements of IEEE 837:2014 : T-Joint, X-Joint, L-Joint , Straight joint
| Supply | Nos. | 25
| Installation | Nos. | 25
49.4 | Supply & Installation of CAPE make UL Listed Maintenance Free Copper bonded Earth rod of 3048mm length having the dia of 17.2 mm with copper coating thickness of 254 microns. The rod has been tested for Dimension, Marking, Tensile Strength, Salt mist, coating thickness, Electrical resistivity test before and after corrosion test as per IEC 62561-2 & UL 467. CAPE Type No. CBR 1710 Supply & Installation of CAPE make earth enchancing mineral compound tested for leaching and TCLP with NABL accredited Lab as per IEC 62561-7 -25 kg CAPE Type: PROSAN 12.5 Supply & Installation of CAPE make Earth rod clamp made for terminating cable / flat conductor. CAPE Type: ERC 1417 SS + CAPE Type: CPES 8 Supply of CAPE make Earth Chamber Inspection Pit made up of Plastic withstand load of 60kN CAPE Type: EC 290
| Supply | Nos. | 2
| Installation | Nos. | 2
50 | PART B @ STRUCTURAL DOWN CONDUCTOR - RISER INSIDE COLUMN
50.1 | Supply & Installation of 10 mm dia copper bonded Solid Steel Round Conductor with minimum coating thickness 100µm for integrated down conductor. Material should be tested Tensile strength, Electrical Resistance, salt mist, Bend & Adhesion to meet the requirements of IS/ IEC 62305 and IEC 62561-1&2. CAPE Type: SRC10CUB
| Supply | Mtrs. | 100
| Installation | Mtrs. | 100
50.2 | Supply & Installation of Multipurpose Bonding clamp for interconnecting Round Conductor with reinforcement rebar inside the concrete to meet the requirements of IS/IEC 62305. CAPE Type: MCBC 101832
| Supply | Nos. | 32
| Installation | Nos. | 32
50.3 | Supply & Installation of Stainless Steel Straight Connector of integrated down conductor and should be tested for electrical resistivity, mechanical load to meet the requirement for IS/IEC - 62305 and IEC 62561-1&2. CAPE Type: SC 8-10
| Supply | Nos. | 32
| Installation | Nos. | 32
50.4 | Supply & Installation of Stainless Steel Earthing stud with fixing clamp accessories of dimension 69X69X205 mm Stainless Steel plate thick ness of 3mm with 10mm dia Copper bonded steel round conductor to connect with reinforment used in structural steel earthing system to meet the requirements of IS/IEC 62305 and IEC 62561-1&2 CAPE Type: ES 1 RA1
| Supply | Nos. | 8
| Installation | Nos. | 8
51 | PART C @ Terrace External Lightning Protection System
51.1 | Supply & Installation of 8mm dia Aluminium alloy Solid Round Conductor of material AlMgSi used in air termination. Cross sectional area of conductor should be 50 mm². Test Parameter: a.Lightning impulse current of 100kA for 10/350 µs b.Electrical resistivity - 0.034 µΩm, c.Tensile strength - 178 MPa or N/mm² d. Salt spray - No Sign of Corrosion. Tested as per IEC 62561-2. CAPE Type: SRC 8 AL
| Supply | Mtrs. | 260
| Installation | Mtrs. | 260
51.2 | Supply & Installation of Nylon Conductor Holder for Parapet wall for holding 8 mm dia Aluminium alloy round Conductor. CAPE Type: PCH 8-S
| Supply | Nos. | 220
| Installation | Nos. | 220
51.3 | Supply & Installation of Nylon roof conductor holder for flat roof with concrete block for fixing 8 mm dia Aluminium alloy Solid Round Conductor in the terrace flat surface at every 1 mtr. CAPE Type: MBPCH8-S
| Supply | Nos. | 40
| Installation | Nos. | 40
51.4 | Supply & Installation of Stainless steel 304 Grade Cross Connector for 8 mm dia Aluminium alloy round conductor at cross/Tee junction. Test Parameter a) Mechanical Load b) Electrical Test c) ENvironmental Test Tested for IEC 62561-1 CAPE Type: CCSS 8-10
| Supply | Nos. | 35
| Installation | Nos. | 35
51.5 | Supply & Installation of Expansion Joint with connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations. Expansion Joint should be consider at every 20 mtr length of straight horizontal air termination and connected at both the end with use of straight connector conductor. CAPE Type: EPC 8
| Supply | Nos. | 11
| Installation | Nos. | 11
51.6 | Supply & Installation of Aluminium Straight conductor connector for interconnecting 8mm Aluminium conductor to meets the requirement of IS/IEC 62305. Test Parametres: a) Mechanical Load b) Electrical Resistivity c) Environmental Test Tested as per IEC 62561-1 CAPE Type: CJ 8
| Supply | Nos. | 16
| Installation | Nos. | 16
51.7 | Supply & Installation of air termination rod of 2mtr length of material AlMgSi of diameter ø 16/10 mm crimped on both the ends (Tapered Type). The rod shall be mounted with stainless steel clamp and fixing accessories . Test Parameter for 2 mtr vertical air terminal a)ELECTRICAL Resistivity b) Tensile Strength c) Condition of Salt Mist Tested as per IEC 62561-2. Test Parameter for Wall clamp a) Mechanical load as per IEC 62561-1 CAPE Type: VAT W2
| Supply | Nos. | 4
| Installation | Nos. | 4
51.8 | Supply & Installation of air termination rod of 2mtr length of material AlMgSi of diameter ø 16/10 mm crimped on both the ends (Tapered Type). The rod shall be mounted with stainless steel clamp and fixing accessories . Test Parameter for 2 mtr vertical air terminal a)ELECTRICAL Resistivity b) Tensile Strength c) Condition of Salt Mist Tested as per IEC 62561-2. Test Parameter for Wall clamp a) Mechanical load as per IEC 62561-1 CAPE Type: VAT F2
| Supply | Nos. | 2
| Installation | Nos. | 2
51.9 | Supply & Installation of Stainless Steel Earthing stud with fixing clamp accessories of dimension 69X69X205 mm Stainless Steel plate thick ness of 3mm with 10mm dia Copper bonded steel round conductor to connect with reinforment used in structural steel earthing system to meet the requirements of IS/IEC 62305 and IEC 62561-1&2 CAPE Type: ES 1 RA1
| Supply | Nos. | 8
| Installation | Nos. | 8
51.10. | Supply & Installation of Stainless steel SS 304 Grade Folding Clamp as per sheet profile for 8 mm dia Aluminium alloy Solid Round Conductor for horizontal Air terminal above metal sheet to meet the requirements for IS/IEC 62305. Test Parameter: a) Mechanical Load b) Environmental Test Tested as per IEC 62561-4 CAPE Type: FSCH 14-8
| Supply | Nos. | 10
| Installation | Nos. | 10
TOTAL PART -H LIGHTNING PROTECTION
PART I :LT PANEL
52.1 | Supply and Installation of Main LT panel Ground floor - As per SLD
| Supply | Nos. | 1
| Installation | Nos. | 1
52.2 | Supply and Installation of Main LT panel First floor - As per SLD
| Supply | Nos. | 1
| Installation | Nos. | 1
52.3 | Supply and Installation of Lighting Main DB- As per SLD
| Supply | Nos. | 1
| Installation | Nos. | 1
TOTAL PART - I
GRAND TOTAL (IIIB)
(IIIC) | TYPICAL ROOM ELECTRICAL WORKS
PART - A : INTERNAL WIRING
Supply & Installation, Testing and Commissioning of point wiring using 2 x 1.5 + 1 R x 1.0 sqmm PVC insulated FRLS multi stranded 1100V grade copper wires drawn in 20mm dia 2mm thick PVC FRLS conduit including all conduit accessories such as bends, Junction boxes etc. The wiring shall be done in complete looping in system. The switches used shall be moulded on orient make MODULE SALUS Make integral GI box with clear earthing facility. The wiring shall be complete with ceiling, switches and all consumables, connectors etc., The lighting circuit number to be placed in switch plate with sticker . (Colour coding of wiring should be adopted)
53.1 | One light point controlled by one switch . {4.5 meters}
| Supply | Nos. | 1016
| Installation | Nos. | 1016
53.2 | One Fan controlled by One no of One way switch with step type electronic regulator. {5.5 meters}
| Supply | Nos. | 508
| Installation | Nos. | 508
TOTAL PART A
PART B : Switch & Socket
54.1 | Supply & Installation of 6A 3/5 pin intel socket controlled by one no. of 6A SP Switch with appropriate factory made GI box. for Raw Power Points with Wiring by using 2R X 1.5Sqmm + 1R x 1Sqmm PVC insulated FRLS drawn 1100V Grade Multistrand Copper Wire in 20mm dia 2mm thick PVC FRLS conduit of approved make including all conduit accessories. (CRABTREE VERNO or equivalent) {3.5meters}
| Supply | Nos. | 4032
| Installation | Nos. | 4032
54.2 | Supply & installation of A/c point. with one no. of 6A 3/5 Pin Socket in Appropriate factory made GI Box, without Switch control and with Wiring by using 2R X 1.5Sqmm + 1R x 1Sqmm PVC insulated FRLS drawn 1100V Grade Multistrand Copper Wire in 20mm dia 2mm thick PVC FRLS conduit of approved make including all conduit accessories. {5 meters}
| Supply | Nos. | RO
| Installation | Nos. | RO
54.3 | Supply & Installation of 2R x 2.5 Sqmm +1Rx1.5 Sqmm PVC insulated FRLS grade multistrand copper wires of approved make - For room LIGHTING AND POWER CIRCUIT
| Supply | Mtrs. | 30480
| Installation | Mtrs. | 30480
54.4 | Supply & Installation of 20 mm dia 2 mm thick FRLS PVC conduit including all conduit accessories - for room circuit conduit.
| Supply | Mtrs. | 30480
| Installation | Mtrs. | 30480
TOTAL PART B
PART C :SUPPLY & INSTALLATION OF LIGHT FIXTURES
Light fitting Lumen Package supplier/vendor to specify.
55.1 | Supply and Installtion of 1x24 Slim LED batten with aluminium housing and diffuser is an ideal replacement solution for existing battens / fluorescent lamps with elegantly designed end caps diffuser to provide glare - free uniform light distribution. High lumen efficacy LED with viewing angle of 120° used to enhance the lumen output make : orient: model LBLN-22-C-SQ-AL Polycarbonate TASKLINE SQ AL clour temp : 5700k
| Supply | Nos. | 1016
| Installation | Nos. | 1016
55.2 | Supply and installation 1 * 56 watts 1200MM Sweep, 320rpm,220CMM. 3 Blade Ceiling Fan. Note: should work with regulator.(study rooms)
Make: Orient , Model: New BREEZE -WHITE
| Supply | Nos. | 508
| Installation | Nos. | 508
TOTAL PART C
GRAND TOTAL (IIIC)
(IIID) | LIGHTNING PROTECTION WORKS
56 | PART A @ RING EARTHING SYSTEM UNDER SOIL
56.1 | Supply & Installation of 10 mm dia copper bonded Solid Steel Round Conductor with minimum coating thickness 100µm for earthing system. Material should be tested Tensile strength, Electrical Resistance, salt mist, Bend & Adhesion to meet the requirements of IS/ IEC 62305 and IEC 62561-1&2. CAPE Type: SRC10CuB
| Supply | Mtrs. | 1000
| Installation | Mtrs. | 1000
56.2 | Supply & Installation of Corrosion Bitumen tape for inside soil. CAPE Type: CT5
| Supply | Nos. | 40
| Installation | Nos. | 40
56.3 | Installation of Exothermic Welding - Including welding mould and other accessories for welding confirms the requirements of IEEE 837:2014 : T-Joint, X-Joint, L-Joint , Straight joint
| Supply | Nos. | 120
| Installation | Nos. | 120
56.4 | Supply & Installation of CAPE make UL Listed Maintenance Free Copper bonded Earth rod of 3048mm length having the dia of 17.2 mm with copper coating thickness of 254 microns. The rod has been tested for Dimension, Marking, Tensile Strength, Salt mist, coating thickness, Electrical resistivity test before and after corrosion test as per IEC 62561-2 & UL 467. CAPE Type No. CBR 1710 Supply & Installation of CAPE make earth enchancing mineral compound tested for leaching and TCLP with NABL accredited Lab as per IEC 62561-7 -25 kg CAPE Type: PROSAN 12.5 Supply & Installation of CAPE make Earth rod clamp made for terminating cable / flat conductor. CAPE Type: ERC 1417 SS + CAPE Type: CPES 8 Supply of CAPE make Earth Chamber Inspection Pit made up of Plastic withstand load of 60kN CAPE Type: EC 290
| Supply | Nos. | 8
| Installation | Nos. | 8
TOTAL OF PART A
57 | PART B @ STRUCTURAL DOWN CONDUCTOR - RISER INSIDE COLUMN
57.1 | Supply & Installation of 10 mm dia copper bonded Solid Steel Round Conductor with minimum coating thickness 100µm for integrated down conductor. Material should be tested Tensile strength, Electrical Resistance, salt mist, Bend & Adhesion to meet the requirements of IS/ IEC 62305 and IEC 62561-1&2. CAPE Type: SRC10CUB
| Supply | Mtrs. | 920
| Installation | Mtrs. | 920
57.2 | Supply & Installation of Multipurpose Bonding clamp for interconnecting Round Conductor with reinforcement rebar inside the concrete to meet the requirements of IS/IEC 62305. CAPE Type: MCBC 101832
| Supply | Nos. | 288
| Installation | Nos. | 288
57.3 | Supply & Installation of Stainless Steel Straight Connector of integrated down conductor and should be tested for electrical resistivity, mechanical load to meet the requirement for IS/IEC - 62305 and IEC 62561-1&2. CAPE Type: SC 8-10
| Supply | Nos. | 288
| Installation | Nos. | 288
57.4 | Supply & Installation of Stainless Steel Earthing stud with fixing clamp accessories of dimension 69X69X205 mm Stainless Steel plate thick ness of 3mm with 10mm dia Copper bonded steel round conductor to connect with reinforment used in structural steel earthing system to meet the requirements of IS/IEC 62305 and IEC 62561-1&2 CAPE Type: ES 1 RA1
| Supply | Nos. | 32
| Installation | Nos. | 32
TOTAL OF PART B
58 | PART C @ Terrace External Lightning Protection System
58.1 | Supply & Installation of 8mm dia Aluminium alloy Solid Round Conductor of material AlMgSi used in air termination. Cross sectional area of conductor should be 50 mm². Test Parameter: a.Lightning impulse current of 100kA for 10/350 µs b.Electrical resistivity - 0.034 µΩm, c.Tensile strength - 178 MPa or N/mm² d. Salt spray - No Sign of Corrosion. Tested as per IEC 62561-2. CAPE Type: SRC 8 AL
| Supply | Mtrs. | 1040
| Installation | Mtrs. | 1040
58.2 | Supply & Installation of Nylon Conductor Holder for Parapet wall for holding 8 mm dia Aluminium alloy round Conductor. CAPE Type: PCH 8-S
| Supply | Nos. | 980
| Installation | Nos. | 980
58.3 | Supply & Installation of Nylon roof conductor holder for flat roof with concrete block for fixing 8 mm dia Aluminium alloy Solid Round Conductor in the terrace flat surface at every 1 mtr. CAPE Type: MBPCH8-S
| Supply | Nos. | 32
| Installation | Nos. | 32
58.4 | Supply & Installation of Stainless steel 304 Grade Cross Connector for 8 mm dia Aluminium alloy round conductor at cross/Tee junction. Test Parameter a) Mechanical Load b) Electrical Test c) ENvironmental Test Tested for IEC 62561-1 CAPE Type: CCSS 8-10
| Supply | Nos. | 120
| Installation | Nos. | 120
58.5 | Supply & Installation of Expansion Joint with connector to compensate the expansion and contraction of Solid Round Al. Conductor during temperature variations. Expansion Joint should be consider at every 20 mtr length of straight horizontal air termination and connected at both the end with use of straight connector conductor. CAPE Type: EPC 8
| Supply | Nos. | 64
| Installation | Nos. | 64
58.6 | Supply & Installation of Aluminium Straight conductor connector for interconnecting 8mm Aluminium conductor to meets the requirement of IS/IEC 62305. Test Parametres: a) Mechanical Load b) Electrical Resistivity c) Environmental Test Tested as per IEC 62561-1 CAPE Type: CJ 8
| Supply | Nos. | 80
| Installation | Nos. | 80
58.7 | Supply & Installaion of air termination rod of 2mtr length of material AlMgSi of diametre ø 16/10 mm crimped on both the ends (Tappered Type). The rod shall be mounted with stainless steel clamp and fixing accessories . Test Parameter for 2 mtr vertical air terminal a)ELectrical Resistivity b) Tensile Strength c) Condition of Salt Mist Tested as per IEC 62561-2. Test Parametrer for Wall clamp a) Mechanical load as per IEC 62561-1 CAPE Type: VAT W2
| Supply | Nos. | 16
| Installation | Nos. | 16
58.8 | Supply & Installation of air termination rod of 2mtr length of material AlMgSi of diametre ø 16/10 mm crimped on both the ends (Tappered Type). The rod shall be mounted with stainless steel clamp and fixing accessories . Test Parameter for 2 mtr vertical air terminal a)ELectrical Resistivity b) Tensile Strength c) Condition of Salt Mist Tested as per IEC 62561-2. Test Parametrer for Wall clamp a) Mechanical load as per IEC 62561-1 CAPE Type: VAT F2
| Supply | Nos. | 12
| Installation | Nos. | 12
58.9 | Supply & Installation of Stainless Steel Earthing stud with fixing clamp accessories of dimension 69X69X205 mm Stainless Steel plate thick ness of 3mm with 10mm dia Copper bonded steel round conductor to connect with reinforment used in structural steel earthing system to meet the requirements of IS/IEC 62305 and IEC 62561-1&2 CAPE Type: ES 1 RA1
| Supply | Nos. | 32
| Installation | Nos. | 32
58.10. | Supply & Installation of Stainless steel SS 304 Grade Folding Clamp as per sheet profile for 8 mm dia Aluminium alloy Solid Round Conductor for horizontal Air terminal above metal sheet to meet the requirements for IS/IEC 62305. Test Parameter: a) Mechanical Load b) Environmental Test Tested as per IEC 62561-4 CAPE Type: FSCH 14-8
| Supply | Nos. | 40
| Installation | Nos. | 40
TOTAL OF PART C
GRAND TOTAL (IIID)
GRAND TOTAL (III)
(IV) | PHE WORKS
(IVA) | PHE WORKS (HOSTEL BLOCKS)
A | SANITARY FIXTURES
WATER CLOSET
59.1 | Supply, Installing, testing and commissioning of White Coloured wall mounted type European Water Closet compatible for 3 & 6 flush with PP soft close seat cover, wallvit pan fittings etc complete as directed by Engineer In Charge. (Concealed cistern shall be paid in line item 3). Make: Jaquar Model: CNS-WHT-963SPP | Each | 212
59.2 | Supply,Installing, testing and commissioning of white coloured Floor mounted type with integral type foot rests Indian Water Closet, with 100 mm P or S trap, necessary pan fittings, including cutting and making good the walls and floors wherever required, extension pvc pipe for concealed tank, etc complete as directed by Engineer In Charge, All joints must be tested for leakage before the final floor finish is applied. (concealed cistern shall be paid in line item 3). Make: Hindware Model: Asian Squatting Pan - 20018 | Each | 28
59.3 | Supply, Installing, testing and commissioning of 1 Nos. Health Faucet with Angle cock (Flow rate 5 Lpm) with necessary accessories, pressure compensating aerator & consumables etc complete. as directed by Engineer In Charge. Make: Jaquar Model: ALD-CHR-573 (Health Faucet) Model: FLP-CHR-5053PM (Angle cock) | Each | 240
59.4 | Supply, Installing, testing and commissioning of Jaquar make in wall tank and cover plate, CI/GI chair bracket, necessary bolt nut, chipping, and restoring the same to original condition, etc., complete as directed by Engineer In Charge. (3 & 6 Ltr dual flush). Tank : Jaquar, Model No : JCS-WHT-2400, Flush Plate : JCP-CHR-152415 | Each | 240
59.5 | Supply, Installing, testing and commissioning of White Color Counter Sunk Wash Basin, The quoted rate should be considering the below mentioned items, necessary accessories/brackets, consumables, pressure compensating aerator etc., complete as directed by Engineer In Charge. | Each | 236
| Wash Basin Make: Jaquar Model No : CNS-WHT-701 |  | 0
| Pillar Cock Make: Jaquar Model : LYR-CHR-38011 - Flow rate 3.78 LPM |  | 0
| 1 No. CP Angular Stop Cock Make: Jaquar Model: Astra-AQT-CHR-3057P |  | 0
| 1 No. 32mm CP P- Trap Make: Omplast/Noway |  | 0
| 1 No. Flexible connection pipe. Makje: Futura/Viking |  | 0
| 1 No. 32 mm Dia CP waste coupling Make: Jaquar/Omplast |  | 0
59.6 | Supply, Installing, testing and commissioning of White Color Wall Hung Wash Basin, The quoted rate should be considering the below mentioned items, necessary accessories/brackets, consumables, pressure compensating aerator etc., complete as directed by Engineer In Charge. | Each | 4
| Wash Basin Make: Jaquar Model No : CNS-WHT-801 |  | 0
| Pillar Cock Make: Jaquar Model : LYR-CHR-38011 - Flow rate 3.78 LPM |  | 0
| 1 No. CP Angular Stop Cock Make: Jaquar Model: Astra-AQT-CHR-3057P |  | 0
| 1 No. 32mm CP P- Trap Make: Omplast/Noway |  | 0
| 1 No. Flexible connection pipe. Makje: Futura/Viking |  | 0
| 1 No. 32 mm Dia CP waste coupling Make: Jaquar/Omplast |  | 0
59.7 | Supply, Installing, testing and commissioning of White Color Flat Back Urinal with Accessories. With comprising of below mentioned items: etc complete as directed by the Engineer In Charge. (0.5 LPF flow rate), (necessary wiring considered under electrical scope) |  | 0
| Urinal with bracket. Make: Jaquar Model: URS-WHT-13253N | Each | 224
| Sensor operated flush valve Make: Askon Model: AS 06 IR E | Each | 224
| SHOWER |  | 0
59.8 | Supply, Installing, testing and commissioning of concealed part of Single Lever Diverter with necessary adapters, chipping, and restoring the same to original condition, accessories, etc., complete as per the Directions of the Engineer In charge. Make: Jaquar Model No : ALD-CHR-065M | Each | 232
59.9 | Supply, Installing, testing and commissioning of Exposed parts for Single Lever Diverter of Jaquar make, Model No : FLP-CHR-5065MKPM, Bath Spout, Make : Jaquar - SPJ-CHR-10429PM, Overhead Shower Make : Jaquar Model: OHS-CHR-1709 with Shower Arm Make : Jaquar of model SHA-CHR-477 with necessary extension nipple, pressure compensating aerator with all fittings and necessary accessories, etc., complete as per the Directions of the Engineer In charge. | Each | 232
| ACCESSORIES |  | 0
59.10. | Supply, Installing, testing and commissioning of below listed Chrome Plated accessories with necessary pressure compensating aerator, consumables etc., complete as per the Directions of the Engineer In charge. |  | 0
| a) Toilet Paper Holder Make: Jaquar Model: ACN-CHR-1155S | Each | 240
| b) Anglecocks Make: Jaquar Model: FLP-CHR-5053PM | Each | 28
| c) Long body Bib cocks Make: Jaquar Model No : FLP-CHR-5037PM, 3.78LPM | Each | 112
| d) SS Foldable Grab bar Make: Euronics/Dolpy | Each | 4
| e) SS Straight Grab bar 450mm long Make: Euronics/Dolphy | Each | 16
| f) Soap Dispenser - Push Button, Capacity: 0.8L, Material: ABS, Finish: White Make : Jaquar Model : SDR-WHT-DJ00010FN | Each | 0
| g) Double Coat Hook Make: Jaquar Model: ACN-CHR-1161N | Each | 240
| h) Hand Dryer, Nuovo Dual Flow, Touch Free Make: Jaquar Model : HDR-SLV-AK2030 | Each | 0
| i) Shower Basket Make: Jaquar Model: ACN-CHR-1177N | Each | 232
| j) Towel Rack Make: Jaquar Model: AKP-CHR-35781PS | Each | 232
| k) Towel Ring Make: Jaquar Model: ACN-CHR-1121BN | Each | 4
59.11 | Supply, installation, testing & commissioning in position of Horizontal Storage type water heater suitable for pressure rating above to 4Kg/scum with heating element with thermostat, 1 Nos. 15mm Dia CP angle valve at inlet, Multi-function Safety Valve with CP copper connecting pipes with wall flanges etc., complete with all inlets, outlets, valves and all other accessories etc., complete. Make: Jaquar / Racold / AO Smith |  | 0
| a) 50 Ltrs Capacity | Each | 232
| b) 15 Ltrs Capacity | Each | 4
59.12 | Supply, Installing, testing and commissioning of approved make Stainless Steel Single Bowl Single Drain Board Sink including necessary Waste Coupling, CP P Trap, Angle cock and Sink Mixer(Jaquar Model No: FLP-CHR-5309PM (6LPM)) etc with necessary Low flow aerator of Neoperl make. complete as directed by Engineer In Charge. | Each | 4
Total for Section - A
B | WATER SUPPLY SYSTEM
60.1 | Supplying, installing, fixing, jointing, testing and commissioning of CPVC pipes of SDR 11 up to 50mm dia, above shall be Schedule 40 grade pipes with Schedule 80 grade fittings such as sockets, unions reducers, long or short bends, elbows, nipples, flanges, checknuts, clamps, z-pieces, Brass male and female adapters, brass FPT Tee, Brass FPT elbow etc., where connection with metal is to be made, along with necessary chasing required for concealing the pipes, rendering the same in CM (1:4), The quoted rate shall include the necessary pipe supports like MS Angles, clamps, hangers, with bolts, nuts and anchor fastners with stud rods of M10/M12 etc. complete including anti corrosive paint /galvanised materials as per standards etc., complete.
Cold water lines
| a) 15mm dia | Rmt | 4072
| b) 20mm dia | Rmt | 508
| c) 25mm dia | Rmt | 388
| d) 32mm dia | Rmt | 632
| e) 40mm dia | Rmt | 1952
| f) 50mm dia | Rmt | 344
| g) 65mm dia | Rmt | 0
60.2 | Hot water pipes with insulation - Concealed pipes 6/9mm thickness, all exposed pipes with 13mm thickness |  | 0
| a) 15mm dia | Rmt | 1013
| b) 20mm dia | Rmt | 0
| c) 25mm dia | Rmt | 0
| d) 32mm dia | Rmt | 0
| e) 40mm dia | Rmt | 0
| f) 50mm dia | Rmt | 0
| g) 65mm dia | Rmt | 0
60.3 | Providing, fixing and testing CPVC valves ( ball valves) of SDR11 grade with necessary consumables etc., complete and as directed by Engineer In Charge. |  | 0
| a) 20 mm Dia | Each | 260
| b) 25 mm Dia | Each | 56
| c) 32 mm Dia | Each | 48
| d) 40 mm Dia | Each | 48
| e) 50 mm Dia | Each | 24
60.4 | Providing, fixing and testing heavy quality CI Butterfly valve Slim seal type of 10kg pressure including suitable E table flanges and nuts and bolts etc., complete and as directed by Engineer In Charge. |  | 0
| a) 65 mm Dia | Each | 24
| b) 80 mm Dia | Each | 16
| c) 100mm Dia | Each | 16
60.5 | Providing and fixing of Electrromagnetic flow meters with BMS Compatiable, quoted rate shall include necessary flanges, adaptors, bolt & nut etc complete |  | 0
| a) 32 mm Dia | Each | 4
| b) 50 mm Dia | Each | 4
60.6 | Providing and fixing Air Release Valve with isolation valve, suitable adopters etc complete. |  | 0
| a) 20mm Dia | Each | 8
60.7 | Providing, fixing wafer type check valve PN 10 with suitable CPVC/ MS flanges, transition fittings, bolt-nuts, accessories etc complete as per the direction of Engineer incharge. |  | 0
| a) 32 mm Dia | Each | 8
| b) 50 mm Dia | Each | 16
60.8 | Providing, fixing wafer type CI Y-Strainer with suitable CPVC/ MS flanges, transition fittings, bolt-nuts, accessories etc complete as per the direction of Engineer incharge. |  | 0
| a) 32 mm Dia | Each | 8
| b) 50 mm Dia | Each | 16
60.9 | Providing, fixing of Diaphargam Float Valve with suitable collars, transition fittings, bolt-nuts, accessories etc complete as per the direction of Engineer incharge. Make: Apex / Watts |  | 0
| a) 32 mm Dia | Each | 4
| b) 50 mm Dia | Each | 4
60.10. | Providing & fixing of electronic BMS compatiable water level indicator with indication of minimum 3 water levels, including accessories etc., complete as per the direction of Engineer-In-Charge.(Fire,Domestic & Flushing Tank) | Each | 8
60.11 | Providing & fixing of suitable copper tinned cable for level controller, the quoted rate shall include necessary suitable size of PVC conduits and fittings etc., complete | Rmt | 600
60.12 | Supplying, fixing and testing inlet, outlet, vent and overflow pipes, fittings with CI frame and cover to over head water tank completeas shown on the drawings etc., complete, accessories comprising of the following. Note : All puddle flanges to be of GI C-class Pipe of upto 600mm Long with 6mm thk MS plate welded at centre, upto 50mm dia threaded end, above Flanged ends. |  | 0
| a) 32 mm Dia | Each | 4
| b) 50 mm Dia | Each | 60
| c) 65 mm Dia | Each | 12
| d) 80 mm Dia | Each | 16
| e) 100 mm Dia | Each | 8
| f) 150mm Dia | Each | 0
| g) FRP Cover with frame 600 x 600mm (MD - 10T) - Make:Aagam/Everlast/HP | Each | 24
60.13 | Supply & fixing of PVC encapsuled Surface mounted rungs for tanks and collection pit with necessary SS anchor fastner, bolt, nut etc.complete. | Nos | 240
60.14 | Construction of Valve chamber of size mentioned below with 230mm thick walls in well burnt table moulded bricks in CM 1.4 over a bed of 100 mm thick PCC 1:4:8 internal walls plastered smooth in CM 1:3 and external walls plastered in 1:3 with sponge finish with all leads and lifts, necessary excavation, backfilling etc., complete. (depth up to 900mm) |  | 0
| a) 600mm x 600mm | Nos | 8
60.15 | Supplying and fixing FRP frame & cover of size and load bearing capacity mentioned below finishing the same with Cement mortor etc complete. As directed by EIC. |  | 0
| a) 600 mm x 600mm - Medium duty (10 MT) | Nos | 8
60.16 | Excavation in all types of soil for laying pipes upto 300mm dia. including forming bottom surface to required level, refilling with available selected excavated earth around the pipe in layers 150mm thick, watering, consolidating and disposing off the surplus earth within the site as directed by the engineer with a lead of 200M etc, providing necessary Shoring & Strutting while excavating etc if necessary complete. -Depth from 0 M upto 1.5 M | Cum | 0
60.17 | Supply, fixing, testing and commissioning of Terrace Booster Pump system with Fully automatic outdoor type control panel with Pump mounted VFD system consisting of Vertical/Horizontal Multistage pumps, connected in Parallel mounted on a common base frame with Discharge manifolds, NRV & Isolating Valves, Pressure Gauge, Pressure Transmitter & Panel. The Panel shall include all required fuses, motor protection, main switch, Pressure Tank. The Supply Includes: 1. Vertical/Horizontal pumps 2. Valves - in suction & discharge header 3. NRV - 1 per pump 4. Base plate 5. Manifold for delivery 6. Pressure tank of suitable capacity. 7. Suitable Motor/Pump Protection Covers For Treated water supply & Flush water supply Pumps - 2 Nos. (1W+ 1S) Flow each pump - 12.5 M3/Hr Head each pump - 20 Mtrs. | Set | 8
Total for Section - B
C | DRAINAGE SYSTEM
61.1 | Providing and fixing PVC "P"traps of self cleaning design with water seal not less than 50mm including setting the trap in 1:2:4 cement concrete in sunken areas or providing suitable support at ceiling level with necessary consumables etc. complete. Trap of 110mm inlet and outlet. | Each | 980
61.2 | Providing and fixing SS Slotted grating of 5"x5" with frame including setting in floor with cement motor to match with floor finish etc., complete. Make: Omplast /Chilly | Each | 980
61.3 | Providing and fixing SS 304 5" x 5" Square frame with SS Dummy grating with screws including setting in floor with cement motor to match with floor finish etc., complete.. Make: Omplast/Chilly | Each | 80
61.4 | Providing and fixing PVC SWR Pipe confirming to IS 13592- TYPE B and fitting as per IS 14735-99 for SOIL & WASTE water discharge, including all fittings with and with out inspection doors, including supports brackets as per supplier specification and distance,cutting, chases/ holes in walls etc., complete. |  | 0
| a) 110 mm Dia | Rm | 4699.2
| b) 160 mm Dia | Rm | 0
61.5 | Providing and fixing PVC Agri pipe as per IS 4985 6Kg/cm2 and fitting for waste pies, including all fittings, supports, brackets as per supplier specification and distance,cutting, chases/holes in walls etc., complete . |  | 0
| a) 40 mm dia - 6Kg/cm2 | Rm | 360
| b) 50 mm dia - 6Kg/cm2 | Rm | 336
| c) 63 mm dia - 4Kg/cm2 - vent pipe in Shaft | Rm | 200
| d) 200 mm Dia - 6Kg/cm2 | Rm | 0
61.6 | Excavation in all types of soil for laying pipes upto 300mm dia. including forming bottom surface to required level, refilling with available selected excavated earth around the pipe in layers 150mm thick, watering, consolidating and disposing off the surplus earth within the site as directed by the engineer with a lead of 200M etc, providing necessary Shoring & Strutting while excavating etc if necessary complete. |  | 0
| a) Depth from 0 M upto 1.5 M | Cum | 0
| b) Depth from 0 M upto 3.0 M | Cum | 0
61.7 | Providing and fixing of gully trap, with brick masonry chamber using table moulded bricks in CM 1:4,over a bed of 75mm thick PCC 1:4:8, internal and external plastering 12mm thick in CM 1:4,including supply and fixing of PVC P-traps. |  | 0
| a) 450 mm x 450 mm Depth up to750mm | Nos | 24
0
61.8 | Construction of Inspection chamber of size mentioned below with 230mm thick walls in well burnt table moulded bricks/Solid block of 200mm thk in CM 1.4 over a bed of 100 mm thick PCC 1:4:8 internal walls plastered smooth in CM 1:3 and external walls plastered in 1:3 with sponge finish with all leads and lifts, necessary excavation, backfilling etc., complete. (depth up to 1200mm) |  | 0
| a) 600mm x 600mm | Nos | 24
61.9 | Providing and fixing of Ready made PE Chambers of required sizes , the quoted rate shall include necessary PCC support, finishing etc., complete. Make: Supreme/Ashirwad |  | 0
| a) 600mm dia, depth up to 1.0mtr | Nos | 0
| b) 600mm dia, depth up to 1.5mtr | Nos | 0
61.10. | Supplying and fixing FRP frame & cover of size and load bearing capacity mentioned below with necessary PCC, finishing the same with Cement mortor etc complete. As directed by EIC. Make Aagam/Everlast |  | 0
| a) 450x450mm - Medium duty (10 MT) | Nos | 20
| b) 600mm x 600mm - Medium duty (10 MT) | Nos | 8
| c) 600mm - Heavy duty ( 20 MT) | Nos | 16
0
61.11 | Providing sleeves in RCC slab [excluding cost of packing] max depth upto 200mm |  | 0
| a. 75mm dia | Each | 240
| b. 150mm dia | Each | 1300
| c. 200mm dia | Each | 40
Total for Section - C
D | RAIN WATER SYSTEM
62.1 | Providing and fixing PVC Agri pipe as per IS 4985 6Kg/cm2 and fitting for waste pies, including all fittings, supports, brackets as per supplier specification and distance,cutting, chases/holes in walls etc., complete .
| a) 110mm dia | Rmt | 600
| b) 160mm dia | Rmt | 500
| c) 200mm dia | Rmt | 0
62.2 | Providing and fixing PVC rain water inlet (Khurra) with aluminium grating, with necessary accessories, consumables etc complete as per the Directions of the Engineer In charge. Make : Sri Vinayaka / Clarion / Equivalent |  | 0
| a) 110mm dia | Each | 24
| b) 160mm dia | Each | 20
| c) 200mm dia | Each | 0
63.3 | Construction of Inspection chamber of size mentioned below with 230mm thick walls in well burnt table moulded bricks/Solid block of 200mm thk in CM 1.4 over a bed of 100 mm thick PCC 1:4:8 internal walls plastered smooth in CM 1:3 and external walls plastered in 1:3 with sponge finish with all leads and lifts, necessary excavation, backfilling etc., complete. (depth up to 750mm) |  | 0
| a) 600mm x 600mm | Nos | 0
64.4 | Supplying and fixing FRP frame & cover of size and load bearing capacity mentioned below with necessary PCC, finishing the same with Cement mortor etc complete. As directed by EIC. |  | 0
| a) 600mm x 600mm - Medium duty (10 MT) - Slotted grating. | Nos | 0
65.5 | Excavation in all types of soil for laying pipes upto 300mm dia. including forming bottom surface to required level, refilling with available selected excavated earth around the pipe in layers 150mm thick, watering, consolidating and disposing off the surplus earth within the site as directed by the engineer with a lead of 200M etc, providing necessary Shoring & Strutting while excavating etc if necessary complete. |  | 0
| a) Depth from 0 M upto 1.5 M | Cum | 0
| b) Depth from 0 M upto 3.0 M | Cum | 0
Total for Section - D
E | HOT WATER SYSTEM
66.1 | Supply, Installation, testing, commissioning of approved make Micro Processor Controlled Air to Water Heat Pump delivering the heating capacity mentioned below. The Heat Pump should consist of Two Scroll Compressors, evaporator & Heat Exchanges . The refrigerant shall be eco-friendly. The system should be complete with Power and Control Cabling Interconnecting the Heat Pump and the Necessary Control Panel. The Heat Pump shall be controlled by necessary Micro processor controllers and shall have BMS Compatibility. Necessary antivibration mounts shall be provided for the Heat Pump. The equipment shall be capable of producing Hot Water upto 60°C. The heat pump shall have inbuilt circulation pump for cirulating hot water between mixing tank and heat pump. The Body of the Heat Pump shall be made of MS Podwer coated, quoted rate shall include lead, lift and positioning of equipment at the required place. The system shall be capable to withstand 5kg/cm2 working pressure and Testing pressure of 10kg/cm2 of cold water inlet pressure. (2Working + 1 standby = 1 set) i. Heating Capacity of each Heat Pump – 26 kW ii. Minimum COP - 4 Note: in case of high usage stand by heat pump shall also work Data Sheet to be submitted by Vendor | Set | RO
66.2 | Supply, installation, testing & commissioning an Mild Steel insulated hot water mixing tank of capacity specified, either vertical or horizontal type as per the space avilability, fabricated out of MS plates. Dished end of 8 mm thick and shell shall be 6 mm thick, complete with inlet cold water, inlet/outlet, drain connection with flanges, manhole with bolted cover, including valves, pressure gauge, dial type thermometer, pressure relief valve complete in all respect as given below. The tank shall be capable of operating pressure of 5kg/cm2 and test pressure of 10kg/cm2 of cold water inlet pressure. The tank shall be insulated with Rockwool of minimum thickness 80mm and shall be provided with 24 guage Aluminium cladding. Sufficient nozzles shall be provided for Inlet/Supply and Return Lines, quoted rate shall include lead, lift and positioning of equipment at the required place. a. 5500 LTRS Epoxy Coating for inner surface of the tank and outer finishing with 1 coat of zinccromate oxide and 2 coat of black enamel paint for corrosion resistant. The Tank Thermal insulation with rockwool with 24 SWG aluminium outer cladding. GA drawing to be sibmitted by Vendor | Each | RO
66.3 | Providing, installation, testing and commissioning of approved make hot water re-circulation pumps (1W+1S) suitable for 400 Volts .M.S.channel, base plate 3-phase electric supply complete with vibration isolators, isolating valve on suction and discharge, non return valve on discharge, pressure gauges and dial type thermometer, rain protection cover etc., complete Flow rate & head - to be filled by vendor | Set | RO
66.4 | Supply, Installation, testing, commissioning of Electrical control panel with all cabling for Integration and automatic operation of the Heat pumps, Hot Water Pumps and the Return Pumps. The control panel shall function based on the set temperatures and set timings with the temperature sensor & timer based control for start and stop of the Heat pump and the circulation pumps with necessary dry running protection for the circulation pumps . etc The Panel shall include the temperature controls for the Mixing tank if any. (Incomer cable to this panel is considered under Electrical package) | set | RO
66.5 | Supplying of High quality flat plate Solar Panels to generate hot water each panel shall be capable of generating 125 LPD, including all required structural support, necessary inlet/ Outlet connecting piping, drain point etc. complete as required. Make:Rashmi/Emvee | No | RO
66.6 | Supply, Installation, testing, commissioning of Solar hot water circulation pumps(1W+1S) suitable for 400 Volts.M.S.channel, base plate 3-phase electric supply complete with vibration isolators, pressure gauges and dial type thermometer etc., complete with control panel with timer and temperature controller for control of operation, rainprotection cover etc complete Flow rate & head - to be filled by vendor | Set | RO
66.7 | The Heat Pumps, tanks & recirculation pumps shall be interconnected with CPVC Piping and necessary Ball valves, NRV. strainer etc. The CPVC pipes shall also be insulated with glass wool and Aluminium cladding including all header lines & vales and tapping provision of MTA/FTA for inlet and outlet connection etc complete. | Lot | RO
66.8 | Supply, Installation, testing, commissioning of Interconnection of solar panels using GI Heavy Grade Pipes with necessary ball valves, Solar Circulation pump and connecting the same to the Storage tank. The piping shall be insulated with glass wool and Aluminium cladding. | Lot | RO
Total for Section - E
F | RO Plant
67.1 | Supply, installation, testing & commissioning of RO plant of 200LPH with FRP pre-filter along with Multi port valve, dosing tank of 100ltr capacity, dosing pump of Milton roy make having flow rate of 0-4 lph to with stand 3.5 kg pressure, RO feed pumps of Grundfos/wilo make, Spiral wound type RO Membrane of make Toray / Dowof size 4040, Recovery (%) rate is 60 to 70%, RO High Pressure Pumps of Grundfos / wilo make of suitable capacity, along with CIP system containing CIP Pumps and CIP tank of 100Ltr capacity including all accessories, Inter connecting piping, with 230 V Electrically operated auto valves, with Dump valve, Control Panel with PLC, pH meter, ORP meter, High & low pressure switches, auto flush timer and storage Tank of SS 316 - Rib type - thickness 1 mm of capacity 1000Ltr, Suitable Motor/Pump Protection Covers.. etc., complete as per the direction of Engineer-In-Charge. | Set | 4
67.2 | Supply, fixing, testing and commissioning of Terrace Booster Pump system with Fully automatic outdoor type control panel with Pump mounted VFD system consisting of Vertical/Horizontal Multistage pumps, connected in Parallel mounted on a common base frame with Discharge manifolds, NRV & Isolating Valves, Pressure Gauge, Pressure Transmitter & Panel. The Panel shall include all required fuses, motor protection, main switch, Pressure Tank. The Supply Includes: 1. Vertical/Horizontal pumps 2. Valves - in suction & discharge header 3. NRV - 1 per pump 4. Base plate 5. Manifold for delivery 6. Pressure tank of suitable capacity. 7. Suitable Motor/Pump Protection Covers For Treated water supply & Flush water supply Pumps - 2 Nos. (1W+ 1S) Flow each pump - 1 M3/Hr Head each pump - 10 Mtrs. | Set | 4
Total for Section - F
TOTAL PHE (Hostel Blocks) IVA (A to F)
(IVB) | PHE WORKS (CAFATERIA)
A | SANITARY FIXTURES
WATER CLOSET
68.1 | Supply, Installing, testing and commissioning of White Coloured wall mounted type European Water Closet compatible for 3 & 6 flush with PP soft close seat cover, wallvit pan fittings etc complete as directed by Engineer In Charge. (Concealed cistern shall be paid in line item 3). Make: Jaquar Model: CNS-WHT-963SPP | Each | 2
68.2 | Supply,Installing, testing and commissioning of white coloured Floor mounted type with integral type foot rests Indian Water Closet, with 100 mm P or S trap, necessary pan fittings, including cutting and making good the walls and floors wherever required, extension pvc pipe for concealed tank, etc complete as directed by Engineer In Charge, All joints must be tested for leakage before the final floor finish is applied. (concealed cistern shall be paid in line item 3). Make: Hindware Model: Asian Squatting Pan - 20018 | Each | RO
68.3 | Supply, Installing, testing and commissioning of 1 Nos. Health Faucet with Angle cock (Flow rate 5 Lpm) with necessary accessories, pressure compensating aerator & consumables etc complete. as directed by Engineer In Charge. Make: Jaquar Model: ALD-CHR-573 (Health Faucet) Model: FLP-CHR-5053PM (Angle cock) | Each | 2
68.4 | Supply, Installing, testing and commissioning of Jaquar make in wall tank and cover plate, CI/GI chair bracket, necessary bolt nut, chipping, and restoring the same to original condition, etc., complete as directed by Engineer In Charge. (3 & 6 Ltr dual flush). Tank : Jaquar, Model No : JCS-WHT-2400, Flush Plate : JCP-CHR-152415 | Each | 2
WASH BASIN
68.5 | Supply, Installing, testing and commissioning of White Color Counter Sunk Wash Basin, The quoted rate should be considering the below mentioned items, necessary accessories/brackets, consumables, pressure compensating aerator etc., complete as directed by Engineer In Charge. | Each | 49
Wash Basin Make: Jaquar Model No : CNS-WHT-701
Pillar Cock Make: Jaquar Model : LYR-CHR-38011 - Flow rate 3.78 LPM
1 No. CP Angular Stop Cock Make: Jaquar Model: Astra-AQT-CHR-3057P
1 No. 32mm CP P- Trap Make: Omplast/Noway
1 No. Flexible connection pipe. Makje: Futura/Viking
1 No. 32 mm Dia CP waste coupling Make: Jaquar/Omplast
68.6 | Supply, Installing, testing and commissioning of White Color Wall Hung Wash Basin, The quoted rate should be considering the below mentioned items, necessary accessories/brackets, consumables, pressure compensating aerator etc., complete as directed by Engineer In Charge. | Each | RO
Wash Basin Make: Jaquar Model No : CNS-WHT-801
Pillar Cock Make: Jaquar Model : LYR-CHR-38011 - Flow rate 3.78 LPM
1 No. CP Angular Stop Cock Make: Jaquar Model: Astra-AQT-CHR-3057P
1 No. 32mm CP P- Trap Make: Omplast/Noway
1 No. Flexible connection pipe. Makje: Futura/Viking
1 No. 32 mm Dia CP waste coupling Make: Jaquar/Omplast
URINAL
68.7 | Supply, Installing, testing and commissioning of White Color Flat Back Urinal with Accessories. With comprising of below mentioned items: etc complete as directed by the Engineer In Charge. (0.5 LPF flow rate), (necessary wiring considered under electrical scope)
| Urinal with bracket. Make: Jaquar Model: URS-WHT-13253N | Each | 2
| Sensor operated flush valve Make: Askon Model: AS 06 IR E | Each | 2
SHOWER
68.8 | Supply, Installing, testing and commissioning of concealed part of Single Lever Diverter with necessary adapters, chipping, and restoring the same to original condition, accessories, etc., complete as per the Directions of the Engineer In charge. Make: Jaquar Model No : ALD-CHR-065M | Each | 2
68.9 | Supply, Installing, testing and commissioning of Exposed parts for Single Lever Diverter of Jaquar make, Model No : FLP-CHR-5065MKPM, Bath Spout, Make : Jaquar - SPJ-CHR-10429PM, Overhead Shower Make : Jaquar Model: OHS-CHR-1709 with Shower Arm Make : Jaquar of model SHA-CHR-477 with necessary extension nipple, pressure compensating aerator with all fittings and necessary accessories, etc., complete as per the Directions of the Engineer In charge. | Each | 2
ACCESSORIES
68.10. | Supply, Installing, testing and commissioning of below listed Chrome Plated accessories with necessary pressure compensating aerator, consumables etc., complete as per the Directions of the Engineer In charge.
| a) Toilet Paper Holder Make: Jaquar Model: ACN-CHR-1155S | Each | 2
| b) Anglecocks Make: Jaquar Model: FLP-CHR-5053PM | Each | 100
| c) Long body Bib cocks Make: Jaquar Model No : FLP-CHR-5037PM, 3.78LPM | Each | 10
| d) SS Foldable Grab bar Make: Euronics/Dolpy | Each | RO
| e) SS Straight Grab bar 450mm long Make: Euronics/Dolphy | Each | RO
| f) Soap Dispenser - Push Button, Capacity: 0.8L, Material: ABS, Finish: White Make : Jaquar Model : SDR-WHT-DJ00010FN | Each | 2
| g) Double Coat Hook Make: Jaquar Model: ACN-CHR-1161N | Each | 2
| h) Hand Dryer, Nuovo Dual Flow, Touch Free Make: Jaquar Model : HDR-SLV-AK2030 | Each | 2
| i) Shower Basket Make: Jaquar Model: ACN-CHR-1177N | Each | 2
| j) Towel Rack Make: Jaquar Model: AKP-CHR-35781PS | Each | 2
| k) Towel Ring Make: Jaquar Model: ACN-CHR-1121BN | Each | RO
68.11 | Supplying, installing, testing and commissioning approved make Electric water heater Including necessary C.P. flexible inlet connection pipes, Rag bolts/expansion bolts etc Complete.
| a) 25 Ltrs Capacity | Each | 8
68.12 | Supply, Installing, testing and commissioning of approved make Stainless Steel Single Bowl Single Drain Board Sink including necessary Waste Coupling, CP P Trap, Angle cock and Sink Mixer(Jaquar Model No: FLP-CHR-5309PM (6LPM)) etc with necessary Low flow aerator of Neoperl make. complete as directed by Engineer In Charge. | Each | RO
Total for Section - A
B | WATER SUPPLY SYSTEM
69.1 | Supplying, installing, fixing, jointing, testing and commissioning of CPVC pipes of SDR 11 up to 50mm dia, above shall be Schedule 40 grade pipes with Schedule 80 grade fittings such as sockets, unions reducers, long or short bends, elbows, nipples, flanges, checknuts, clamps, z-pieces, Brass male and female adapters, brass FPT Tee, Brass FPT elbow etc., where connection with metal is to be made, along with necessary chasing required for concealing the pipes, rendering the same in CM (1:4), The quoted rate shall include the necessary pipe supports like MS Angles, clamps, hangers, with bolts, nuts and anchor fastners with stud rods of M10/M12 etc. complete including anti corrosive paint /galvanised materials as per standards etc., complete.
Cold water lines
| a) 15mm dia | Rmt | 400
| b) 20mm dia | Rmt | 300
| c) 25mm dia | Rmt | 200
| d) 32mm dia | Rmt | 150
| e) 40mm dia | Rmt | 150
| f) 50mm dia | Rmt | 40
| g) 65mm dia | Rmt | 30
69.2 | Hot water pipes with insulation - Concealed pipes 6/9mm thickness, all exposed pipes with 13mm thickness
| a) 15mm dia | Rmt | 120
| b) 20mm dia | Rmt | 30
| c) 25mm dia | Rmt | RO
| d) 32mm dia | Rmt | RO
| e) 40mm dia | Rmt | RO
| f) 50mm dia | Rmt | RO
| g) 65mm dia | Rmt | RO
69.3 | Providing, fixing and testing CPVC valves ( ball valves) of SDR11 grade with necessary consumables etc., complete and as directed by Engineer In Charge.
| a) 20 mm Dia | Each | 30
| b) 25 mm Dia | Each | 10
| c) 32 mm Dia | Each | 10
| d) 40 mm Dia | Each | 10
| e) 50 mm Dia | Each | RO
69.4 | Providing, fixing and testing heavy quality CI Butterfly valve Slim seal type of 10kg pressure including suitable E table flanges and nuts and bolts etc., complete and as directed by Engineer In Charge.
| a) 65 mm Dia | Each | 6
| b) 80 mm Dia | Each | RO
| c) 100mm Dia | Each | RO
69.5 | Providing and fixing of Electrromagnetic flow meters with BMS Compatiable, quoted rate shall include necessary flanges, adaptors, bolt & nut etc complete
| a) 32 mm Dia | Each | 1
| b) 40 mm Dia | Each | 1
69.6 | Providing and fixing Air Release Valve with isolation valve, suitable adopters etc complete.
| a) 20mm Dia | Each | 2
69.7 | Providing, fixing wafer type check valve PN 10 with suitable CPVC/ MS flanges, transition fittings, bolt-nuts, accessories etc complete as per the direction of Engineer incharge.
| a) 32 mm Dia | Each | 1
| b) 40 mm Dia | Each | 1
69.8 | Providing, fixing wafer type CI Y-Strainer with suitable CPVC/ MS flanges, transition fittings, bolt-nuts, accessories etc complete as per the direction of Engineer incharge.
| a) 32 mm Dia | Each | 1
| b) 40 mm Dia | Each | 1
69.9 | Providing, fixing of Diaphargam Float Valve with suitable collars, transition fittings, bolt-nuts, accessories etc complete as per the direction of Engineer incharge. Make: Apex / Watts
| a) 32 mm Dia | Each | 1
| b) 40 mm Dia | Each | 1
69.10. | Providing & fixing of electronic BMS compatiable water level indicator with indication of minimum 3 water levels, including accessories etc., complete as per the direction of Engineer-In-Charge.(Fire,Domestic & Flushing Tank) | Each | 3
69.11 | Providing & fixing of suitable copper tinned cable for level controller, the quoted rate shall include necessary suitable size of PVC conduits and fittings etc., complete | Rmt | 300
69.12 | Supplying, fixing and testing inlet, outlet, vent and overflow pipes, fittings with CI frame and cover to over head water tank completeas shown on the drawings etc., complete, accessories comprising of the following. Note : All puddle flanges to be of GI C-class Pipe of upto 600mm Long with 6mm thk MS plate welded at centre, upto 50mm dia threaded end, above Flanged ends.
| a) 32 mm Dia | Each | 1
| b) 50 mm Dia | Each | 15
| c) 65 mm Dia | Each | 3
| d) 80 mm Dia | Each | 4
| e) 100 mm Dia | Each | 2
| f) 150mm Dia | Each | RO
| g) FRP Cover with frame 600 x 600mm (MD - 10T) - Make:Aagam/Everlast/HP | Each | 6
69.13 | Supply & fixing of PVC encapsuled Surface mounted rungs for tanks and collection pit with necessary SS anchor fastner, bolt, nut etc.complete. | Nos | 60
69.14 | Construction of Valve chamber of size mentioned below with 230mm thick walls in well burnt table moulded bricks in CM 1.4 over a bed of 100 mm thick PCC 1:4:8 internal walls plastered smooth in CM 1:3 and external walls plastered in 1:3 with sponge finish with all leads and lifts, necessary excavation, backfilling etc., complete. (depth up to 900mm)
| a) 600mm x 600mm | Nos | 1
69.15 | Supplying and fixing FRP frame & cover of size and load bearing capacity mentioned below finishing the same with Cement mortor etc complete. As directed by EIC.
| a) 600 mm x 600mm - Medium duty (10 MT) | Nos | 1
69.16 | Excavation in all types of soil for laying pipes upto 300mm dia. including forming bottom surface to required level, refilling with available selected excavated earth around the pipe in layers 150mm thick, watering, consolidating and disposing off the surplus earth within the site as directed by the engineer with a lead of 200M etc, providing necessary Shoring & Strutting while excavating etc if necessary complete. -Depth from 0 M upto 1.5 M | Cum | 10
69.17 | Supply, fixing, testing and commissioning of Terrace Booster Pump system with Fully automatic outdoor type control panel with Pump mounted VFD system consisting of Vertical/Horizontal Multistage pumps, connected in Parallel mounted on a common base frame with Discharge manifolds, NRV & Isolating Valves, Pressure Gauge, Pressure Transmitter & Panel. The Panel shall include all required fuses, motor protection, main switch, Pressure Tank. The Supply Includes: 1. Vertical/Horizontal pumps 2. Valves - in suction & discharge header 3. NRV - 1 per pump 4. Base plate 5. Manifold for delivery 6. Pressure tank of suitable capacity. 7. Suitable Motor/Pump Protection Covers For Treated water supply Pumps - 2 Nos. (1W+ 1S) Flow each pump - 12.5 M3/Hr Head each pump - 20 Mtrs. | Set | RO
Total for Section - B
C | DRAINAGE SYSTEM
70.1 | Providing and fixing PVC "P"traps of self cleaning design with water seal not less than 50mm including setting the trap in 1:2:4 cement concrete in sunken areas or providing suitable support at ceiling level with necessary consumables etc. complete. Trap of 110mm inlet and outlet. | Each | 35
70.2 | Providing and fixing SS Slotted grating of 5"x5" with frame including setting in floor with cement motor to match with floor finish etc., complete. Make: Omplast /Chilly | Each | 85
70.3 | Providing and fixing SS 304 5" x 5" Square frame with SS Dummy grating with screws including setting in floor with cement motor to match with floor finish etc., complete.. Make: Omplast/Chilly | Each | 4
70.4 | Providing and fixing PVC SWR Pipe confirming to IS 13592- TYPE B and fitting as per IS 14735-99 for SOIL & WASTE water discharge, including all fittings with and with out inspection doors, including supports brackets as per supplier specification and distance,cutting, chases/ holes in walls etc., complete.
| a) 110 mm Dia | Rm | 500
| b) 160 mm Dia | Rm | RO
70.5 | Providing and fixing PVC Agri pipe as per IS 4985 6Kg/cm2 and fitting for waste pies, including all fittings, supports, brackets as per supplier specification and distance,cutting, chases/holes in walls etc., complete .
| a) 40 mm dia - 6Kg/cm2 | Rm | 90
| b) 50 mm dia - 6Kg/cm2 | Rm | 120
| c) 63 mm dia - 4Kg/cm2 - vent pipe in Shaft | Rm | 60
| d) 200 mm Dia - 6Kg/cm2 | Rm | RO
70.6 | Excavation in all types of soil for laying pipes upto 300mm dia. including forming bottom surface to required level, refilling with available selected excavated earth around the pipe in layers 150mm thick, watering, consolidating and disposing off the surplus earth within the site as directed by the engineer with a lead of 200M etc, providing necessary Shoring & Strutting while excavating etc if necessary complete.
| a) Depth from 0 M upto 1.5 M | Cum | 10
| b) Depth from 0 M upto 3.0 M | Cum | RO
70.7 | Providing and fixing of gully trap, with brick masonry chamber using table moulded bricks in CM 1:4,over a bed of 75mm thick PCC 1:4:8, internal and external plastering 12mm thick in CM 1:4,including supply and fixing of PVC P-traps.
| a) 450 mm x 450 mm Depth up to750mm | Nos | 3
70.8 | Construction of Inspection chamber of size mentioned below with 230mm thick walls in well burnt table moulded bricks/Solid block of 200mm thk in CM 1.4 over a bed of 100 mm thick PCC 1:4:8 internal walls plastered smooth in CM 1:3 and external walls plastered in 1:3 with sponge finish with all leads and lifts, necessary excavation, backfilling etc., complete. (depth up to 1200mm)
| a) 600mm x 600mm | Nos | 3
70.9 | Providing and fixing of Ready made PE Chambers of required sizes , the quoted rate shall include necessary PCC support, finishing etc., complete. Make: Supreme/Ashirwad
| a) 600mm dia, depth up to 1.0mtr | Nos | RO
| b) 600mm dia, depth up to 1.5mtr | Nos | RO
70.10. | Supplying and fixing FRP frame & cover of size and load bearing capacity mentioned below with necessary PCC, finishing the same with Cement mortor etc complete. As directed by EIC. Make Aagam/Everlast
| a) 450x450mm - Medium duty (10 MT) | Nos | 3
| b) 600mm x 600mm - Medium duty (10 MT) | Nos | 3
| c) 600mm - Heavy duty ( 20 MT) | Nos | RO
70.11 | Providing sleeves in RCC slab [excluding cost of packing] max depth upto 200mm
| a. 75mm dia | Each | 15
| b. 150mm dia | Each | 20
| c. 200mm dia | Each | 4
70.12 | Supplying, installing, testing and commissioning of Cast iron centrifugally cast pipes as per IS 3989 : 2005 with necessary fittings like bends, shoes , Y fittings , tee's, plugs, collars etc., laid under floor. The jointing method shall be drip seal compound joint & proportion of the drip seal application shall be as per the manufacturer's recommendation.-For Kitchen draiange Make: Neco/BIC/Kapilansh
| a) 100mm dia | Rm | 250
| b) 150mm dia | Rm | 120
70.13 | Supplying, fixing, testing & commissioning of 100mm dia cast iron deep water seal P trap as per IS 3989 : 2005 with necessary CI boss connections with a minimum 2Nos. of 50mm dia inlets. The trap shall be supported with PCC etc.., complete. Make: Neco/BIC/Kapilansh. | Each | 50
70.14 | Supplying, installing, testing and commissioning of approved make below ground type grease trap of PE body complaint with EN 1825, with inlet, outlet and baffle fittings, height adjustable top cover. the trap shall be one-piece construction. the quoted rate shall include necessary consumbles as per the manufacturer's recommendation. Size : NS 5.5 Make: ACO/Kessel | Each | 1
Total for Section - C
D | RAIN WATER SYSTEM
71.1 | Providing and fixing PVC Agri pipe as per IS 4985 6Kg/cm2 and fitting for waste pies, including all fittings, supports, brackets as per supplier specification and distance,cutting, chases/holes in walls etc., complete .
| a) 110mm dia | Rmt | 20
| b) 160mm dia | Rmt | 30
| c) 200mm dia | Rmt | 90
71.2 | Providing and fixing PVC rain water inlet (Khurra) with aluminium grating, with necessary accessories, consumables etc complete as per the Directions of the Engineer In charge. Make : Sri Vinayaka / Clarion / Equivalent
| a) 110mm dia | Each | 4
| b) 160mm dia | Each | 2
| c) 200mm dia | Each | 6
71.3 | Construction of Inspection chamber of size mentioned below with 230mm thick walls in well burnt table moulded bricks/Solid block of 200mm thk in CM 1.4 over a bed of 100 mm thick PCC 1:4:8 internal walls plastered smooth in CM 1:3 and external walls plastered in 1:3 with sponge finish with all leads and lifts, necessary excavation, backfilling etc., complete. (depth up to 750mm)
| a) 600mm x 600mm | Nos | 8
71.4 | Supplying and fixing FRP frame & cover of size and load bearing capacity mentioned below with necessary PCC, finishing the same with Cement mortor etc complete. As directed by EIC.
| a) 600mm x 600mm - Medium duty (10 MT) - Slotted grating. | Nos | 8
71.5 | Excavation in all types of soil for laying pipes upto 300mm dia. including forming bottom surface to required level, refilling with available selected excavated earth around the pipe in layers 150mm thick, watering, consolidating and disposing off the surplus earth within the site as directed by the engineer with a lead of 200M etc, providing necessary Shoring & Strutting while excavating etc if necessary complete.
| a) Depth from 0 M upto 1.5 M | Cum | 30
| b) Depth from 0 M upto 3.0 M | Cum | RO
Total for Section - D
E | RO Plant
72.1 | Supply, installation, testing & commissioning of RO plant of 250LPH with FRP pre-filter along with Multi port valve, dosing tank of 100ltr capacity, dosing pump of Milton roy make having flow rate of 0-4 lph to with stand 3.5 kg pressure, RO feed pumps of Grundfos/wilo make, Spiral wound type RO Membrane of make Toray / Dowof size 4040, Recovery (%) rate is 60 to 70%, RO High Pressure Pumps of Grundfos / wilo make of suitable capacity, along with CIP system containing CIP Pumps and CIP tank of 100Ltr capacity including all accessories, Inter connecting piping, with 230 V Electrically operated auto valves, with Dump valve, Control Panel with PLC, pH meter, ORP meter, High & low pressure switches, auto flush timer and storage Tank of SS 316 - Rib type - thickness 1 mm of capacity 2000Ltr, Suitable Motor/Pump Protection Covers.. etc., complete as per the direction of Engineer-In-Charge. | Set | 1
Total for Section - E
TOTAL PHE ( Cafateria) IVB (A to E)
GRAND TOTAL PHE IV (IVA+IVB)
(V) | FAPA WORKS
(VA) | FAPA WORKS (HOSTEL BLOCKS)
A | Fire Alarm System (HOSTEL BLOCKS)
73 | Microprocessor based intelligent addressable, modular, expandable networkable, fire alarm control panel with minimum 960 character LCD display, multiple access levels, event history file in non-violatile memory (EPROM). The panel shall display and control all point in the entire network from the front keypad. The panel shall be equipped with sufficient number of loops, each loop shall have capacity of minimum 250 addressable devices in one loop.The panel shall have 240 Volts AC Power supply, automatic battery charger with RS 485 Network card. The panel shall be provided with Modbus module for BMS interface
73.1 | 1 nos 8- loop panel with 2 loop card. Make: Bosch
| Supply | Set | 4
| Installation | Set | 4
73.2 | Supply and Installation of power supply unit with battery for sounder.Make:Bosch
| Supply | Set | 8
| Installation | Set | 8
73.3 | Supply and Installation of power supply unit with battery for FAS panel.Make:Bosch
| Supply | Set | 4
| Installation | Set | 4
74 | RESPONSE INDICATORS:
Supply and Installation of Response indicator led TYPE mounting base etc, MAKE: Bosch
| Supply | Nos. | 0
| Installation | Nos. | 0
75 | ABOVE and Below SMOKE DETECTOR :
Addressable analogue multi sensor detector with base, with built in fault isolation module MAKE: Bosch
| Supply | Nos. | 1320
| Installation | Nos. | 1320
76 | STROBE WITH SOUNDER (Loop Sounder)
Supply, Installation, Testing & Commissioning of Strobe Lights Cum Hooter with 110 cd. The strobes shall be synchronized for better evacuation.MAKE:Bosch
| Supply | Nos. | 236
| Installation | Nos. | 236
77 | ADDRESSABLE CHARGED POWER SUPPLY FOR STROBE WITH SOUNDER
Supply, Installation, Testing & Commissioning of Addressable Charged Power Supply for STROBE WITH SOUNDER . MAKE: Bosch
| Supply | Nos. | 236
78 | MANUAL CALL POINT:
Supply, Installation, Testing & Commissioning of Manual Call Point MAKE: Bosch
| Supply | Nos. | 236
| Installation | Nos. | 236
79 | CONTROL MODULE:
Supply, Installation, Testing & Commissioning of Addressable Control Module, MAKE: Bosch
| Supply | Nos. | 96
| Installation | Nos. | 96
80 | MONITOR MODULE:
Supply, Installation, Testing & Commissioning of Addressable Monitor Module,MAKE:Bosch
| Supply | Nos. | 0
81 | RELAY MODULE:
Supply, Installation, Testing & Commissioning of Addressable Control Relay Module, MAKE: Bosch
| Supply | Nos. | 12
| Installation | Nos. | 12
82 | BEAM DETECTOR
Supply, Installation, Testing & Commissioning of Addressable Beam Detector MAKE: Bosch
| Supply | Nos. | 24
| Installation | Nos. | 24
82.1 | Supply and Installation Signalling interface module
| Supply | Nos. | 60
| Installation | Nos. | 60
82.2 | Supply and Installation of Multi sensor detaector electrical and DB room
| Supply | Nos. | 80
| Installation | Nos. | 80
83 | The GUI based main network software
Supply, Installation, Testing & Commissioning of The GUI based main network software must be capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems; and / or sensors’ locations. The GUI software shall be located in control room in one of the blocks and shall monitor all the blocks panel connected with each other. The software shall be capable of monitoring 100 Nodes with more than 20 MB baud Transmission rate on Fiber Optics Network and 10 MB baud Transmission on cable or more. The software shall provide the facility to Monitor, Control all the Digital PAVA as well as 2 way communication from main control room using voice signals over Fire Network along with the Fire detection signal. MAKE: Bosch
| Supply | Nos. | 4
| Installation | Nos. | 4
84 | Supply and Installation of 2 core 1.5 Sqmm copper FRLS flexible cable with all accessories for Detectors and control module power supply cable.
| Supply | Mtrs. | 10440
| Installation | Mtrs. | 10440
84.1 | Supply and Installation of 2 core 1.5 Sqmm copper FRLS Ar cable with all accessories for false ceiling area and shaft vertical riser
| Supply | Mtrs. | 3760
| Installation | Mtrs. | 3760
85 | Supply and Installation of 2C x 1.5 Sqmm copper FRLS twisted shielded cable with all accessories for Sounder's power.
| Supply | Mtrs. | 5292
| Installation | Mtrs. | 5292
86 | Supply and installation of combiner box to fix, TBS, MCP, Hooter & speaker inside staircase
| Supply | Nos. | 96
| Installation | Nos. | 96
87 | Supply and Installtion of 25dia 2mm thick FRLS PVC conduit with accessories
| Supply | Mtrs. | 13824
| Installation | Mtrs. | 13824
88 | Supply and Installtion of 100x100MM PVC truff
| Supply | Mtrs. | 40
| Installation | Mtrs. | 40
89 | Supply and Installtion 300x50 GI Raceway with cover for shaft vertical riser
| Supply | Mtrs. | 192
| Installation | Mtrs. | 192
TOTAL OF FAS SYSTEM (A)
B | Public Address System (HOSTEL BLOCKS)
90.1 | Erection, Testing & Commissioning of Microprocessor controlled main control panel with feedback speaker.inclusive of Goose-neck microphone,480W Amplifier and Public Address System console. 8 plena voice control. Make: Bosch
| Supply | Nos. | 4
| Installation | Nos. | 4
90.2 | Supply, testing and commissioning of microprocessor controlled Router for additional loops capable of handling 7 additional zones Make: Bosch
| Supply | Nos | 4
| Installation | Nos. | 4
90.3 | Supply, testing and commissioning of amplifier of 480 watts Make: Bosch
| Supply | Nos | 4
| Installation | Nos | 4
90.4 | Supply, testing and commissioning of amplifier of 240 watts Make: Bosch
| Supply | Nos | RO
| Installation | Nos | RO
91 | PUBLIC ADDRESS SPEAKERS
91.1 | Supplying, installing, testing and commissioning of 6W ceiling mounted type UL listed speakers with multi-tapping capable to produce minimum sound level of 75db at 3m distance. Make: Bosch
| Supply | Nos. | 140
| Installation | Nos. | 140
91.2 | Supplying, installing, testing and commissioning of 6 W wall mounted type UL listed speakers with multi-tapping capable to produce minimum sound level of 75db at 3m distance. Make: Bosch
| Supply | Nos. | RO
| Installation | Nos. | RO
91.3 | Supply and installation of 1.5 Sqmm x 2 core FRLS copper twisted shielded cable for public address system.
| Supply | Mtr. | 5292
| Installation | Mtr. | 5292
92 | Supply and Installtion of 25dia 2mm thick FRLS PVC conduit with accessories
| Supply | Mtrs. | 5082.8
| Installation | Mtrs. | 5082.8
TOTAL OF PAS SYSTEM (B)
C | Talk Back System (HOSTEL BLOCKS)
93 | Supply, Erection, Testing & Commissioning of Microprocessor controlled control panel with feedback speaker. Inclusive of Goose-neck microphone, Amplifier and Multizone System console. 20 Zone (Rack Mount) with DB selector(Ground +17floors each floor 4 staircase) Make: Innovative/Royale
| Supply | Set | 4
| Installation | Set | 4
94 | TALK BACK SPEAKERS
94.1 | Flush Wall mounted talk back speaker 6W with perforated, Manual Call pinhooker Press to talk combain with one compoff Box Make: Innovative
MS Enclosure (Red)
| Supply | Nos. | 96
| Installation | Nos. | 96
94.2 | Supply and installation of 1.5 Sqmm x 2 core FRLS copper Flexible cable for public address system, for talk back speaker
| Supply | Mtr. | 10116
| Installation | Mtr. | 10116
94.3 | Supply and Installtion of 25dia 2mm thick FRLS PVC conduit with accessories
| Supply | Mtrs. | 10116
| Installation | Mtrs. | 10116
TOTAL OF TALK BACK SYSTEM ( C)
TOTAL FAPA(Hostels) VA (A to C)
(VB) | FAPA WORKS (Cafeteria))
A | Fire Alarm System (Cafeteria)
95 | Microprocessor based intelligent addressable, modular, expandable networkable, fire alarm control panel with minimum 960 character LCD display, multiple access levels, event history file in non-violatile memory (EPROM). The panel shall display and control all point in the entire network from the front keypad. The panel shall be equipped with sufficient number of loops, each loop shall have capacity of minimum 250 addressable devices in one loop.The panel shall have 240 Volts AC Power supply, automatic battery charger with RS 485 Network card. The panel shall be provided with Modbus module for BMS interface
95.1 | 1 nos 8- loop panel with 1 loop card. Make: Bosch
| Supply | Set | 1
| Installation | Set | 1
95.2 | Supply and Installation of power supply unit with battery for sounder.Make:Bosch
| Supply | Set | 2
| Installation | Set | 2
95.3 | Supply and Installation of power supply unit with battery for FAS panel.Make:Bosch
| Supply | Set | 1
| Installation | Set | 1
96 | RESPONSE INDICATORS:
Supply and Installation of Response indicator led TYPE mounting base etc, MAKE: Bosch
| Supply | Nos. | 2
| Installation | Nos. | 2
97 | ABOVE and Below SMOKE DETECTOR :
Addressable analogue multi sensor detector with base, with built in fault isolation module MAKE: Bosch
| Supply | Nos. | 49
| Installation | Nos. | 49
98 | ABOVE and Below Heat detector DETECTOR : Kitchen
Addressable analogue multi sensor detector with base, with built in fault isolation module MAKE: Bosch
| Supply | Nos. | 38
| Installation | Nos. | 38
99 | STROBE WITH SOUNDER (Loop Sounder)
Supply, Installation, Testing & Commissioning of Strobe Lights Cum Hooter with 110 cd. The strobes shall be synchronized for better evacuation.MAKE:Bosch
| Supply | Nos. | 10
| Installation | Nos. | 10
100 | ADDRESSABLE CHARGED POWER SUPPLY FOR STROBE WITH SOUNDER
Supply, Installation, Testing & Commissioning of Addressable Charged Power Supply for STROBE WITH SOUNDER . MAKE: Bosch
| Supply | Nos. | 10
| Installation | Nos. | 10
101 | MANUAL CALL POINT:
Supply, Installation, Testing & Commissioning of Manual Call Point MAKE: Bosch
| Supply | Nos. | 10
| Installation | Nos. | 10
102 | CONTROL MODULE:
Supply, Installation, Testing & Commissioning of Addressable Control Module, MAKE: Bosch
| Supply | Nos. | 4
| Installation | Nos. | 4
103 | MONITOR MODULE:
Supply, Installation, Testing & Commissioning of Addressable Monitor Module,MAKE:Bosch
| Supply | Nos. | 0
| Installation | Nos. | 0
104 | RELAY MODULE:
Supply, Installation, Testing & Commissioning of Addressable Control Relay Module, MAKE: Bosch
| Supply | Nos. | 1
| Installation | Nos. | 1
105.1 | BEAM DETECTOR
Supply, Installation, Testing & Commissioning of Addressable Beam Detector MAKE: Bosch
| Supply | Nos. | 4
| Installation | Nos. | 4
105.2 | Supply and Installation Signalling interface module
| Supply | Nos. | 15
| Installation | Nos. | 15
105.3 | Supply and Installation of Multi sensor detector electrical and DB room
| Supply | Nos. | 20
| Installation | Nos. | 20
106 | The GUI based main network software
Supply, Installation, Testing & Commissioning of The GUI based main network software must be capable of graphically representing each facility being monitored with floor plans and icons depicting the actual locations of the various systems; and / or sensors’ locations. The GUI software shall be located in control room in one of the blocks and shall monitor all the blocks panel connected with each other. The software shall be capable of monitoring 100 Nodes with more than 20 MB baud Transmission rate on Fiber Optics Network and 10 MB baud Transmission on cable or more. The software shall provide the facility to Monitor, Control all the Digital PAVA as well as 2 way communication from main control room using voice signals over Fire Network along with the Fire detection signal. MAKE: Bosch
| Supply | Nos. | 1
| Installation | Nos. | 1
106.1 | Supply and Installation of 2 core 1.5 Sqmm copper FRLS flexible cable with all accessories for Detectors and control module power supply cable.
| Supply | Mtrs. | 765
| Installation | Mtrs. | 765
106.2 | Supply and Installation of 2 core 1.5 Sqmm copper FRLS Ar cable with all accessories for false ceiling area and shaft vertical riser
| Supply | Mtrs. | 40
| Installation | Mtrs. | 40
107 | Supply and Installation of 2C x 1.5 Sqmm copper FRLS twisted shielded cable with all accessories for Sounder's power.
| Supply | Mtrs. | 329
| Installation | Mtrs. | 329
108 | Supply and installation of combiner box to fix, TBS, MCP, Hooter & speaker inside staircase
| Supply | Nos. | 0
| Installation | Nos. | 0
109.1 | Supply and Installtion of 25dia 2mm thick FRLS PVC conduit with accessories
| Supply | Mtrs. | 801
| Installation | Mtrs. | 801
109.2 | Supply and Installtion of 25dia 1.6mm thick GI conduit with accessories- Kitchen
| Supply | Mtrs. | 300
| Installation | Mtrs. | 300
110 | Supply and Installtion of 100x100MM PVC truff
| Supply | Mtrs. | 20
| Installation | Mtrs. | 20
111 | Supply and installtion of 150x50mm1.6mm GI raceway with cover with in Shaft
| Supply | Mtrs. | 12
| Installation | Mtrs. | 12
TOTAL OF FAS SYSTEM (Cafeteria) (A)
B | Public Address System (Cafeteria)
112.1 | Erection, Testing & Commissioning of Microprocessor controlled main control panel with feedback speaker.inclusive of Goose-neck microphone,480W Amplifier and Public Address System console. 6 plena voice control. Make: Bosch
| Supply | Nos. | 1
| Installation | Nos. | 1
112.2 | Supply, testing and commissioning of microprocessor controlled Router for additional loops capable of handling 6 additional zones Make: Bosch
| Supply | Nos | 1
| Installation | Nos. | 1
112.3 | Supply, testing and commissioning of amplifier of 480 watts Make: Bosch
| Supply | Nos | Ro
| Installation | Nos | RO
112.4 | Supply, testing and commissioning of amplifier of 240 watts Make: Bosch
| Supply | Nos | 2
| Installation | Nos | 2
113 | PUBLIC ADDRESS SPEAKERS
113.1 | Supplying, installing, testing and commissioning of 6W ceiling surface mounted type UL listed speakers with multi-tapping capable to produce minimum sound level of 75db at 3m distance. Make: Bosch
| Supply | Nos. | 24
| Installation | Nos. | 24
113.2 | Supplying, installing, testing and commissioning of 6 W wall mounted type UL listed speakers with multi-tapping capable to produce minimum sound level of 75db at 3m distance. Make: Bosch
| Supply | Nos. | RO
| Installation | Nos. | RO
113.3 | Supply and installation of 1.5 Sqmm x 2 core FRLS copper twisted shielded cable for public address system.
| Supply | Mtr. | 329
| Installation | Mtr. | 329
113.4 | Supply and Installtion of 25dia 2mm thick FRLS PVC conduit with accessories
| Supply | Mtrs. | 328.1
| Installation | Mtrs. | 328.1
TOTAL OF PAS (Cafeteria) (B)
TOTAL FAPA(Cafeteria) VB (A+B)
GRAND TOTAL FAPA V (VA+VB)
(VI) | NETWORKING AND CAMERA CABLING WORKS
(VIA) | NETWORKING AND CAMERA CABLING WORKS (HOSTEL BLOCKS)
114.1 | CAT-6 UTP CABLE FOR DATA
Supply and Installtion of Category 6 UTP cable. Performance specified to 650 MHz, minimum 5dB next performance above Category-6 UL ad CUL listed. (For Data) 305MTR BOX LSZH MAKE:3C, Make- Comscope/ Client Approved
| Supply | Mtr | 45140
| Installation | Mtr | 45140
114.2 | Supply and Installtion of 3C Make- Cat6 RJ45 Information Outlets with face plate -DATA, Make- Comscope/ Client Approved
| Supply | Nos. | 1768
| Installation | Nos. | 1768
114.3 | Charges for Testing and Documentation of cat6 Nodes
| Installation | Nos. | 1768
Note : Excluding Camera ,server and associated works
TOTAL OF Networking and Camera cabling ( Hostels) (A)
(VIB) | NETWORKING AND CAMERA CABLING WORKS (CAFETERIA)
115.1 | CAT-6 UTP CABLE FOR DATA
Supply and Installtion of Category 6 UTP cable. Performance specified to 650 MHz, minimum 5dB next performance above Category-6 UL ad CUL listed. (For Data) 305MTR BOX LSZH MAKE:3C, Comscope/ Client Approved
| Supply | Mtr | 2440
| Installation | Mtr | 2440
115.2 | Supply and Installtion of 3C Make- Cat6 RJ45 Information Outlets with face plate -DATA, Comscope/ Client Approved
| Supply | Nos. | 68
| Installation | Nos. | 68
115.3 | Charges for Testing and Documentation of cat6 Nodes
| Installation | Nos. | 68
Note : Excluding Camera ,server and associated works
TOTAL OF Networking and Camera cabling (Cafeteria) (B)
GRAND TOTAL Networking & Camera cabling VI (VIA+VIB)
(VII) | FIRE PROTECTION WORKS
(VIIA) | Fire Protection works (HOSTEL BLOCKS)
A | TERRACE PUMPS & ACCESSORIES
116.1 | Supplying installing, testing, and commissioning of BOOSTER PUMP with Control Panel of 900LPM at 35 mtr head. Squirrel cage, TEFC induction motor suitable for 415 ± 6%V, 3 phase, 50 Hz A.C. supply of suitable H.P. pump running at 2900 r.p.m. conforming to IP 55 pralecting and class 'F' insulation. The motor shall be conform to IS:325-1978 (upto date). Both Pump & Motor are to be mounted on common base of requisite strength manufactured out of M.S. channel as per manufacturer's recommendation. with flange, bolt, nut, fittings, Motor & Pump guard shall be provided with thin Aluminium sheet for complete protection etc complete. The cost shall also be inclusive of Terrace pump controller. Make: Kirloskar/Lubi | Nos | 4
116.2 | Supply and laying of following cables with necessary glands, lugs, etc. complete. Make Polycab/Finolex/Havels
| a) 4 core x 16 sq mm aluminium Armored cable | Rmt | 160
| b) 2 core x 2.5 sq mm Copper Flexible cable | Rmt | 160
| c) 4 core x 2.5 sq mm aluminium Armored cable | Rmt | 160
| d) Supplying and fixing 8 SWG COPPER WIRE For pumps equipment | Rmt | 400
116.3 | Supplying and fixing of factory-made perforated Hot-Dip Galvanized (HDG) G. I sheet Cable Trays with necessary angle iron suspension supports, anchor fasteners etc. complete.
| a) 100 x 50 mm x 2mm thick Perforated cable tray | Rmt | 160
116.4 | Above Ground piping - Supply, Installation, Testing and Commissioning of GI C Class pipes confirming to IS 1239 Pt - I &II with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanised), clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows (25mm to 50mm Socket welded type, 65mm and above ERW butt welded fitting), flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The pipes shall be painted with one coat of primer & 2 coats of enamel paint using approved type, MS supports at standard spacing, anchor fasteners, G.I. bolts and nuts, clamps, rails "U" & threaded bolt, Including cutting, Welding, fixing in / on walls, ceiling by using the HI tech / MS supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls, making bore holes in masonry walls / floor and making them good with filler material and finished in cement morter etc. complete in the opening for pipes passing through walls, masonry walls as instructed by site engineer. However in case of sealing the fire walls, application of fire sealant shall be separately paid. The supports like fabricated structural steel support ,wire steel thread, U Clamps threaded rods and concrete pedestal shall be included in the cost. The supports will be hot dip galvanized. Pipes upto 65mm dia shall be with hanger supports with anchor fasteners. 80mm dia and above pipes shall be with structural steel supports. Pipe Make : Jindal Star / Tata Welded Fittings : Goyal / Montex Paint : Asian / Berger
| a) 100 mm nominal dia | Rmt | 96
| b) 150 mm nominal dia | Rmt | RO
116.5 | Supplying, installing and commissionning CI flanged brass "Y" strainer with suitable flanges, nuts and bolts, gaskets, flanges, etc… complete.Make Zoloto/KARTAR
| a) 100 mm nominal dia | Nos | 4
| b) 150 mm nominal dia | Nos | RO
116.6 | Supplying, installing , testing and commisioning Dual plate Wafer type check valve with PN 16 Rating as per IS 5312 with required flanges, nuts, bolts and gaskets etc.complete.Make Zoloto/H sarker/ Kartar
| a) 100 mm nominal dia | Nos | 4
| b) 150 mm nominal dia | Nos | RO
116.7 | Supplying, installing , testing and commisioning CI butterfly valve (PN 16) slim seal standard lever operated type confirming to BS 5155 with required flanges, nuts, bolts etc complete.Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | 8
| b) 150 mm nominal dia | Nos | RO
116.8 | Supplying, installing , testing and commisioning of Forged Brass Ball valve as per IS 778 with all fittings etc complete.Make:Zoloto/RB/Kartar
| a) 25 mm nominal dia | Nos | 4
116.9 | Suppling and installing pressure switch with 12/15 mm Ø isolation valve, G.I. Nipple, elbow etc. in an approved manner.Make:Danfoss/Indfoss | Nos | 4
116.10. | Supplying and installing pressure guage glycerine filled of 100mm Ø, 0 - 300 PSI or 0 - 21 kg/cm2 fitted in syphon tube with 15mm ball valve and G.I pipe, Nipple , elbow etc. as per requirement in an approved manner. (Callibration certificate from manufacturer to be submitted by vendor). Make: H. GURU / FIEBIG / HD | Nos | 4
116.11 | Supplying and installing of 25 mm Ø Forged brass air release valve, with necessary accessories and consumable. Make: Leader/RB/ Zoloto | Nos | 4
Total Part (A)
B | INTERNAL HYDRANT SYSTEM
117.1 | Supply, Installation, Testing and Commissioning of GI C Class pipes confirming to IS 1239 Pt - I &II with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanised), clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows (25mm to 50mm Socket welded type, 65mm and above ERW butt welded fitting), flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The pipes shall be painted with one coat of primer & 2 coats of enamel paint using approved type, MS supports at standard spacing, anchor fasteners, G.I. bolts and nuts, clamps, rails "U" & threaded bolt, Including cutting, Welding, fixing in / on walls, ceiling by using the HI tech / MS supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls, making bore holes in masonry walls / floor and making them good with filler material and finished in cement morter etc. complete in the opening for pipes passing through walls, masonry walls as instructed by site engineer. However in case of sealing the fire walls, application of fire sealant shall be separately paid. The supports like fabricated structural steel support ,wire steel thread, U Clamps threaded rods and concrete pedestal shall be included in the cost. The supports will be hot dip galvanized. Pipes upto 65mm dia shall be with hanger supports with anchor fasteners. 80mm dia and above pipes shall be with structural steel supports. Pipe Make : Jindal Star / Tata Welded Fittings : Goyal / Montex Paint : Asian / Berger
| a) 25 mm nominal dia | Rmt | 24
| b) 32 mm nominal dia | Rmt | RO
| c) 40 mm nominal dia | Rmt | RO
| d) 50 mm nominal dia | Rmt | RO
| e) 65 mm nominal dia | Rmt | RO
| f) 80 mm nominal dia | Rmt | 24
| g) 100 mm nominal dia | Rmt | 120
| h) 150 mm nominal dia | Rmt | RO
117.2 | Supplying, installing , testing and commisioning of CI butterfly valve (PN 16) slim seal standerd lever operated type confirming to IS 13039 with required flanges, nuts, bolts etc complete. Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | RO
| b) 150 mm nominal dia | Nos | RO
117.3 | Supply, installing, testing and commissioning of Single headed oblique hydrant valve as per IS: 5290 type-A, made of SS with 63mm dia instantaneous out lets & 80mm dia flanged inlet, blank PVC cap, chain & hand wheels etc complete as required.. Make :Newage/Kartar/Safeguard | Nos | 28
117.4 | Supply, installing, testing and commissioning of 1 No of 63 mm SS branch pipe with hexagonal detachable 16 mm SS nozzle confirming IS:903, suitable for instantaneous connection to interconnect hose pipe couplings as required. Make :Newage/Kartar/Safeguard | Nos | 28
117.5 | Supply, installing, testing and commissioning of Hose reel complete with 19 mm dia high pressurehose of 40 mtr long with nozzle mounted in a revolving drum ,shut off nozzle as ABS jet & spray nozzle ,with an 25mm ball vale ..complete set. As per IS 884. Make :Newage/Kartar/Safeguard | Nos | 28
117.6 | Supply and fixing of 63 mm dia RRL hose tested to a bursting pressure of 32 Kg / sq.cm made of superior quality cotton and nylon jacket beaming seamless woven and rot proofed each of length 15 mtrs x 2nos. Complete with heavy quality GM coupling Make :Newage/Kartar/Safeguard | set | 28
117.7 | Supply & sealing of all services shafts with Fire stop mortar system Hilti CP 636 firestops/ fire barrier with fire rating of 2 hour, approved by CBRI roorkee, It shall have good adhesion properties with base materials like concrete, masonry, metal pipes. It shall prevent passage of fire, smoke and water through fire rated wall and floor penetrations, cladding, etc. It shall be used as a permanent fire seal for Fire pipes. complete as per the directions of Engineer in charge. | Sq.Mtr | 120
Total Part (B)
C | INTERNAL SPRINKLER SYSTEM
118.1 | Supply, Installation, Testing and Commissioning of GI C Class pipes confirming to IS 1239 Pt - I &II with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanised), clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows (25mm to 50mm DI threaded type, 65mm and above ERW butt welded fitting), flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The pipes shall be painted with one coat of primer & 2 coats of enamel paint using approved type, MS supports at standard spacing, anchor fasteners, G.I. bolts and nuts, clamps, rails "U" & threaded bolt, Including cutting, Welding, fixing in / on walls, ceiling by using the HI tech / MS supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls, making bore holes in masonry walls / floor and making them good with filler material and finished in cement morter etc. complete in the opening for pipes passing through walls, masonry walls as instructed by site engineer. However in case of sealing the fire walls, application of fire sealant shall be separately paid. The supports like fabricated structural steel support ,wire steel thread, U Clamps threaded rods and concrete pedestal shall be included in the cost. The supports will be hot dip galvanized. Pipes upto 65mm dia shall be with hanger supports with anchor fasteners. 80mm dia and above pipes shall be with structural steel supports. Pipe Make : Jindal Star / Tata DI Threaded Fittings : Neu G / Jainsons Butt Welded Fittings : Goyal / Montex Paint : Asian / Berger
| a) 25 mm nominal dia | Rmt | RO
| b) 32 mm nominal dia | Rmt | RO
| c) 40 mm nominal dia | Rmt | RO
| d) 50 mm nominal dia | Rmt | RO
| e) 65 mm nominal dia | Rmt | RO
| f) 80 mm nominal dia | Rmt | RO
| g) 100 mm nominal dia | Rmt | RO
| h) 150 mm nominal dia | Rmt | RO
118.2 | Supplying, installing , testing and commisioning CI butterfly valve (PN 16) slim seal standerd lever operated type confirming to IS 13039 with required flanges, nuts, bolts etc complete. Make Audco/Intervalve/Kartar
| a) 80 mm nominal dia | Nos | RO
| b) 100 mm nominal dia | Nos | RO
118.3 | Supply, installation, testing & commissioning of conventional std coverage/ extended coverage, std response quartzoid bulb/concealed type sprinkler with 15mm screwed end connection of 68°C temperature rating, K-factor & orifice shall not be less than 6mm. Sprinklers shall be UL Listed . Make : Tyco / Viking
| Std. response, std coverage pendent sprinkler - ( K=5.6 ) | Nos | RO
| Std. response std coverage upright sprinkler - ( K=5.6 ) | Nos | RO
| Std. response, std coverage concealed type pendent sprinkler - ( K=5.6 ) | Nos | RO
| Std. response standard coverage sidewall sprinkler - ( K=5.6 ) | Nos | RO
118.4 | Supply installing, testing & commissioning of Installation Control Valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve and all other necessary components as per manufacturer's specifications complete as required.Size :150mm Make Tyco/HD Fire | set | RO
118.5 | Supply installing, testing & commissioning of U.L.listed Braided flexible sprinkler pipe droplet for 12 kg/ sq. cm. working pressure with 1/2" or 3/4" BSP threaded outlet & 1" BSP threaded inlet with reducer nipple, snap, clamp, T-bar bracket etc. with necessary fitting complete as required. Make:Newage/HDfire
| a) 1200 mm length | Each | RO
| b) 1500 mm length | Each | RO
118.6 | Supply installing, testing & commissioning of electrically operated water flow switches (Paddle type) including tamper switch and accessories, complete with tap off socket arrangement as required, with potential free contact with 2 Nos. NONC.. Make Honeywell/System sensor
| a) 80 mm nominal dia | Nos | RO
| b) 100 mm nominal dia | Nos | RO
118.7 | Supply installing, testing & commissioning of inspectors test & drain assembly complete with test valve, sight glass sectional drain valve, union; necessary piping, threading, jointing & with corrosion resistant orifice all complete strictly as per drawing. Make Tyco/HD Fire/Newage
| a) 50mm | set | RO
Total Part (C)
D | EXTERNAL HYDRANT SYSTEM
119.1 | under Ground Piping - Supply installing, testing & commissioning of heavy grade GI pipes confirming to IS: 1239 Part - 1 with maleable specials confirming to IS 1239 P1 and II such as tees, elbows, checknuts, unions flanges, nipples, etc. including cutting welding fixing in/on walls, celling by using as per drawing. The quoted rate shall include PCC support blocks of suitable size etc. Fittings upto 50 mm Threaded Joint, above shall be Butt welded type. The rate quoted should e included with anticorrosive treatment with 4 mm thick polymer corrosion resistant tape as per IS 10221, overlap shall be 15mm minimum. Make:Jindal Hissar/Tata
| a) 80 mm nominal dia | Rmt | RO
| b) 100 mm nominal dia | Rmt | 80
| c) 150 mm nominal dia | Rmt | RO
119.2 | Supply installing, testing & commissioning of CI butterfly valve (PN 16) slim seal standerd lever operated type confirming to IS 13039 with required flanges, nuts, bolts etc complete.Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | 4
| b) 150 mm nominal dia | Nos | RO
119.3 | Supply, installing, testing and commissioning of Single headed oblique hydrant valve as per IS: 5290 type-A, made of SS with 63mm dia instantaneous out lets & 80mm dia flanged inlet, blank PVC cap, chain & hand wheels etc complete as required.. Make :Newage/Kartar/Safeguard | Nos | RO
119.4 | Supply, installing, testing and commissioning of 1 No of 63 mm SS branch pipe with hexagonal detachable 16 mm SS nozzle confirming IS:903, suitable for instantaneous connection to interconnect hose pipe couplings as required. Make :Newage/Kartar/Safeguard | Nos | RO
119.5 | Supply installing, testing & commissioning of Hose boxes of size 750 x 600 x 250 made of FRP (Fibre reinforced plastic) with glass fronted door, painted red outside and white inside with support/ stand to hydrant with additional supports. | Nos | RO
119.6 | Supply and fixing of 63 mm dia RRL hose tested to a bursting pressure of 32 Kg / sq.cm made of superior quality cotton and nylon jacket beaming seamless woven and rot proofed each of length 15 mtrs x 2nos. Complete with heavy quality GM coupling Make :Newage/Kartar/Safeguard | set | RO
119.7 | Supply, installation, testing & commissioning of 2 way fire brigade(IS :904) inlet connection with 63mm dia built-in SS non-return valves instantaneous coupling type with necessary acceessories . Quoted rate shall be suitable size with mounting supports etc. complete. Make :Newage/Kartar/Safeguard | Nos | 4
119.8 | Exacavation of trenches up to 1.5 mts. in depth, for laying pipes upto 150mm dia. Including forming bottom surface to required level, refilling the trenches with selected excavated earth around the pipe in layers of 150mm thick, watering, consolidating. Quoted price inclusive of disposing off / Carting away the surplus earth within the site to a dump yard as directed by the site engineer with a lead of 300 mts. etc. complete.
| a) Excavation in all kinds of soil | Cum | 72
| b) Cutting of Rock with chiselling | Cum | RO
119.9 | Construction of valve chamber with 230 mm best quality TM bricks(50kg/sqcm) in CM 1:4 over a bed of 100 mm thick PCC1:4:8, internal walls plastered smooth with necessary water proof compound in CM 1:3 and external walls plastered rough with sponge finish including curing with all necessary leads and lift and providing Medium duty FRP cover with frame (10 ton of make Aagam/ Everlast/HP) of size 900 x900 mm. Etc., Including Top slab of 300mm etc Complete.
| a) Size 1.2m x 0.9m upto depth of 1.2m (clear dimension) | Nos | 4
Total Part (D)
E | EXTINGUISHERS
120.1 | ABC FIRE EXTINGUISHER 2Kg : Supply and install in position approved make ABC Stored pressure type Fire Extinguisher 2 Kgs Capacity Mono Ammonium Phosphate based Dry Chemical Powder as per IS 14609 with ISI Mark for Fighting ABC Class of Fire, stored Pressure type of Mild steel body pressurized by Nitrogen Gas. The Extinguisher shall have pressure gauge for indicating inside pressure with opening and closing lever of squeeze grip type with tamper proof seal, complete with wall bracket. The Extinguisher is manufactured strictly as per IS: 15683:2006 with ISI mark | Nos | 112
120.2 | ABC FIRE EXTINGUISHER 6Kg : Supply and install in position approved make ABC Stored pressure type Fire Extinguisher 6 Kgs Capacity Mono Ammonium Phosphate based Dry Chemical Powder as per IS 14609 with ISI Mark for Fighting ABC Class of Fire, stored Pressure type of Mild steel body pressurized by Nitrogen Gas. The Extinguisher shall have pressure gauge for indicating inside pressure with opening and closing lever of squeeze grip type with tamper proof seal, complete with wall bracket. The Extinguisher is manufactured strictly as per IS: 15683:2006 with ISI mark. | Nos | 84
120.3 | CO2 FIRE EXTINGUISHER 4.5Kg : Supply and install in position approved make Co2 type Fire Extinguisher 4.5 Kgs Capacity, made from brand new seamless cylinder, as per IS: 7285 and CCE approval, fitted with 1 metre length Wire Braided Discharge hose and horn and Wheel type (ISI Approved) valve with wall bracket and with initial Charge as per IS: 15683-2006specification, bearing ISI Mark. | Nos | 36
120.4 | CO2 FIRE EXTINGUISHER 2Kg : Supply and install in position approved make Co2 type Fire Extinguisher 2.0 Kgs Capacity, made from brand new seamless cylinder, as per IS: 7285 and CCE approval, fitted with 1 metre length Wire Braided Discharge hose and horn and Wheel type (ISI Approved) valve with wall bracket and with initial Charge as per IS: 15683. | Nos | 12
120.5 | WATER MIST FIRE EXTINGUISHER 9.0 Ltr : Supply, Installation & Commissioining of 9Lts. Water mist type fire extinguisher, with initial filling in brand new seamless cylinder with powder coated finish, fitted with Gun Metel, stored pressure type, EPDM flexible discharge hose pipe, Squeeze grip type open/close lever, Limit proof seal, wall mounting bracket etc. complete, confirming to latest IS:15683 code. | Nos | RO
120.6 | FIRE BUCKET : Supplying of Fire Bucket of 24 guage, galvanized steel sheet, standard 9Lts capacity and of round bottom shape, painted white inside and red outside and black on the bottom dome with letters 'FIRE' in black and gold with wall mounting bracket and screws. The rate shall include the cost of river sand. Each set shall have 2Nos. | Set | RO
120.7 | FIRE BUCKET STAND : Fire bucket stand fabricated by MS angles to install 2 Nos. of buckets. | Nos | RO
Total Part (E)
TOTAL of fire protection works (Hostel) VIIA (A to E)
(VIIB) | Fire Protection works (CAFATERIA)
A | TERRACE PUMPS & ACCESSORIES
121.1 | Supplying installing, testing, and commissioning of BOOSTER PUMP with Control Panel of 900LPM at 35 mtr head. Squirrel cage, TEFC induction motor suitable for 415 ± 6%V, 3 phase, 50 Hz A.C. supply of suitable H.P. pump running at 2900 r.p.m. conforming to IP 55 pralecting and class 'F' insulation. The motor shall be conform to IS:325-1978 (upto date). Both Pump & Motor are to be mounted on common base of requisite strength manufactured out of M.S. channel as per manufacturer's recommendation. with flange, bolt, nut, fittings, Motor & Pump guard shall be provided with thin Aluminium sheet for complete protection etc complete. The cost shall also be inclusive of Terrace pump controller. Make: Kirloskar/Lubi | Nos | RO
121.2 | Supply and laying of following cables with necessary glands, lugs, etc. complete. Make Polycab/Finolex/Havels
| a) 4 core x 16 sq mm aluminium Armored cable | Rmt | RO
| b) 2 core x 2.5 sq mm Copper Flexible cable | Rmt | RO
| c) 4 core x 2.5 sq mm aluminium Armored cable | Rmt | RO
| d) Supplying and fixing 8 SWG COPPER WIRE For pumps equipment | Rmt | RO
121.3 | Supplying and fixing of factory-made perforated Hot-Dip Galvanized (HDG) G. I sheet Cable Trays with necessary angle iron suspension supports, anchor fasteners etc. complete.
| a) 100 x 50 mm x 2mm thick Perforated cable tray | Rmt | RO
121.4 | Above Ground piping - Supply, Installation, Testing and Commissioning of GI C Class pipes confirming to IS 1239 Pt - I &II with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanised), clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows (25mm to 50mm Socket welded type, 65mm and above ERW butt welded fitting), flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The pipes shall be painted with one coat of primer & 2 coats of enamel paint using approved type, MS supports at standard spacing, anchor fasteners, G.I. bolts and nuts, clamps, rails "U" & threaded bolt, Including cutting, Welding, fixing in / on walls, ceiling by using the HI tech / MS supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls, making bore holes in masonry walls / floor and making them good with filler material and finished in cement morter etc. complete in the opening for pipes passing through walls, masonry walls as instructed by site engineer. However in case of sealing the fire walls, application of fire sealant shall be separately paid. The supports like fabricated structural steel support ,wire steel thread, U Clamps threaded rods and concrete pedestal shall be included in the cost. The supports will be hot dip galvanized. Pipes upto 65mm dia shall be with hanger supports with anchor fasteners. 80mm dia and above pipes shall be with structural steel supports. Pipe Make : Jindal Star / Tata Welded Fittings : Goyal / Montex Paint : Asian / Berger
| a) 100 mm nominal dia | Rmt | 36
| b) 150 mm nominal dia | Rmt | RO
121.5 | Supplying, installing and commissionning CI flanged brass "Y" strainer with suitable flanges, nuts and bolts, gaskets, flanges, etc… complete.Make Zoloto/KARTAR
| a) 100 mm nominal dia | Nos | 1
| b) 150 mm nominal dia | Nos | RO
121.6 | Supplying, installing , testing and commisioning Dual plate Wafer type check valve with PN 16 Rating as per IS 5312 with required flanges, nuts, bolts and gaskets etc.complete.Make Zoloto/H sarker/ Kartar
| a) 100 mm nominal dia | Nos | 1
| b) 150 mm nominal dia | Nos | RO
121.7 | Supplying, installing , testing and commisioning CI butterfly valve (PN 16) slim seal standard lever operated type confirming to BS 5155 with required flanges, nuts, bolts etc complete.Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | 2
| b) 150 mm nominal dia | Nos | RO
121.8 | Supplying, installing , testing and commisioning of Forged Brass Ball valve as per IS 778 with all fittings etc complete.Make:Zoloto/RB/Kartar
| a) 25 mm nominal dia | Nos | 2
121.9 | Suppling and installing pressure switch with 12/15 mm Ø isolation valve, G.I. Nipple, elbow etc. in an approved manner.Make:Danfoss/Indfoss | Nos | RO
121.10. | Supplying and installing pressure guage glycerine filled of 100mm Ø, 0 - 300 PSI or 0 - 21 kg/cm2 fitted in syphon tube with 15mm ball valve and G.I pipe, Nipple , elbow etc. as per requirement in an approved manner. (Callibration certificate from manufacturer to be submitted by vendor). Make: H. GURU / FIEBIG / HD | Nos | RO
121.11 | Supplying and installing of 25 mm Ø Forged brass air release valve, with necessary accessories and consumable. Make: Leader/RB/ Zoloto | Nos | 2
Total Part (A)
B | INTERNAL HYDRANT SYSTEM
122.1 | Above Ground piping - Supply, Installation, Testing and Commissioning of GI C Class pipes confirming to IS 1239 Pt - I &II with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanised), clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows (25mm to 50mm Socket welded type, 65mm and above ERW butt welded fitting), flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The pipes shall be painted with one coat of primer & 2 coats of enamel paint using approved type, MS supports at standard spacing, anchor fasteners, G.I. bolts and nuts, clamps, rails "U" & threaded bolt, Including cutting, Welding, fixing in / on walls, ceiling by using the HI tech / MS supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls, making bore holes in masonry walls / floor and making them good with filler material and finished in cement morter etc. complete in the opening for pipes passing through walls, masonry walls as instructed by site engineer. However in case of sealing the fire walls, application of fire sealant shall be separately paid. The supports like fabricated structural steel support ,wire steel thread, U Clamps threaded rods and concrete pedestal shall be included in the cost. The supports will be hot dip galvanized. Pipes upto 65mm dia shall be with hanger supports with anchor fasteners. 80mm dia and above pipes shall be with structural steel supports. Pipe Make : Jindal Star / Tata Welded Fittings : Goyal / Montex Paint : Asian / Berger
| a) 25 mm nominal dia | Rmt | 6
| b) 32 mm nominal dia | Rmt | RO
| c) 40 mm nominal dia | Rmt | RO
| d) 50 mm nominal dia | Rmt | RO
| e) 65 mm nominal dia | Rmt | RO
| f) 80 mm nominal dia | Rmt | 6
| g) 100 mm nominal dia | Rmt | 12
| h) 150 mm nominal dia | Rmt | RO
122.2 | Supplying, installing , testing and commisioning of CI butterfly valve (PN 16) slim seal standerd lever operated type confirming to IS 13039 with required flanges, nuts, bolts etc complete. Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | RO
| b) 150 mm nominal dia | Nos | RO
122.3 | Supply, installing, testing and commissioning of Single headed oblique hydrant valve as per IS: 5290 type-A, made of SS with 63mm dia instantaneous out lets & 80mm dia flanged inlet, blank PVC cap, chain & hand wheels etc complete as required.. Make :Newage/Kartar/Safeguard | Nos | 2
122.4 | Supply, installing, testing and commissioning of 1 No of 63 mm SS branch pipe with hexagonal detachable 16 mm SS nozzle confirming IS:903, suitable for instantaneous connection to interconnect hose pipe couplings as required. Make :Newage/Kartar/Safeguard | Nos | 2
122.5 | Supply, installing, testing and commissioning of Hose reel complete with 19 mm dia high pressurehose of 40 mtr long with nozzle mounted in a revolving drum ,shut off nozzle as ABS jet & spray nozzle ,with an 25mm ball vale ..complete set. As per IS 884. Make :Newage/Kartar/Safeguard | Nos | 2
122.6 | Supply and fixing of 63 mm dia RRL hose tested to a bursting pressure of 32 Kg / sq.cm made of superior quality cotton and nylon jacket beaming seamless woven and rot proofed each of length 15 mtrs x 2nos. Complete with heavy quality GM coupling Make :Newage/Kartar/Safeguard | set | 2
122.7 | Supply & sealing of all services shafts with Fire stop mortar system Hilti CP 636 firestops/ fire barrier with fire rating of 2 hour, approved by CBRI roorkee, It shall have good adhesion properties with base materials like concrete, masonry, metal pipes. It shall prevent passage of fire, smoke and water through fire rated wall and floor penetrations, cladding, etc. It shall be used as a permanent fire seal for Fire pipes. complete as per the directions of Engineer in charge. | Sq.Mtr | 10
Total Part (B)
C | INTERNAL SPRINKLER SYSTEM
123.1 | Above Ground piping - Supply, Installation, Testing and Commissioning of GI C Class pipes confirming to IS 1239 Pt - I &II with painting, suitable type of supports, anchor fasteners, bolts nuts (Galvanised), clamps, "U" bolt, malleable specials such as Reducers,Tees, elbows (25mm to 50mm DI threaded type, 65mm and above ERW butt welded fitting), flanges. Including cutting, Welding, fixing in / on walls, ceiling by using suitable supports etc, as per drawings. The pipes shall be painted with one coat of primer & 2 coats of enamel paint using approved type, MS supports at standard spacing, anchor fasteners, G.I. bolts and nuts, clamps, rails "U" & threaded bolt, Including cutting, Welding, fixing in / on walls, ceiling by using the HI tech / MS supports etc, as per drawings. The quoted rate shall also include for chasing / chipping walls, making bore holes in masonry walls / floor and making them good with filler material and finished in cement morter etc. complete in the opening for pipes passing through walls, masonry walls as instructed by site engineer. However in case of sealing the fire walls, application of fire sealant shall be separately paid. The supports like fabricated structural steel support ,wire steel thread, U Clamps threaded rods and concrete pedestal shall be included in the cost. The supports will be hot dip galvanized. Pipes upto 65mm dia shall be with hanger supports with anchor fasteners. 80mm dia and above pipes shall be with structural steel supports. Pipe Make : Jindal Star / Tata DI Threaded Fittings : Neu G / Jainsons Butt Welded Fittings : Goyal / Montex Paint : Asian / Berger
| a) 25 mm nominal dia | Rmt | 366
| b) 32 mm nominal dia | Rmt | 48
| c) 40 mm nominal dia | Rmt | 60
| d) 50 mm nominal dia | Rmt | 78
| e) 65 mm nominal dia | Rmt | 42
| f) 80 mm nominal dia | Rmt | 18
| g) 100 mm nominal dia | Rmt | 60
| h) 150 mm nominal dia | Rmt | 12
123.2 | Supplying, installing , testing and commisioning CI butterfly valve (PN 16) slim seal standerd lever operated type confirming to IS 13039 with required flanges, nuts, bolts etc complete. Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | 2
| b) 150 mm nominal dia | Nos | RO
123.3 | Supply, installation, testing & commissioning of conventional std coverage/ extended coverage, std response quartzoid bulb/concealed type sprinkler with 15mm screwed end connection of 68°C temperature rating, K-factor & orifice shall not be less than 6mm. Sprinklers shall be UL Listed . Make : Tyco / Viking
| Std. response, std coverage pendent sprinkler - ( K=5.6 ) | Nos | 162
| Std. response std coverage upright sprinkler - ( K=5.6 ) | Nos | RO
| Std. response, std coverage concealed type pendent sprinkler - ( K=5.6 ) | Nos | RO
| Std. response standard coverage sidewall sprinkler - ( K=5.6 ) | Nos | RO
| Std. response, std coverage pendent sprinkler - ( K=5.6 ), 141 °C | Nos | 34
123.4 | Supply installing, testing & commissioning of Installation Control Valve with turbine type automatic Alarm Gong to be connected with control valve, drain & test valve and all other necessary components as per manufacturer's specifications complete as required.Size :150mm Make Tyco/HD Fire | set | 1
123.5 | Supply installing, testing & commissioning of U.L.listed Braided flexible sprinkler pipe droplet for 12 kg/ sq. cm. working pressure with 1/2" or 3/4" BSP threaded outlet & 1" BSP threaded inlet with reducer nipple, snap, clamp, T-bar bracket etc. with necessary fitting complete as required. Make:Newage/HDfire
| a) 1200 mm length | Each | RO
| b) 1500 mm length | Each | RO
123.6 | Supply installing, testing & commissioning of electrically operated water flow switches (Paddle type) including tamper switch and accessories, complete with tap off socket arrangement as required, with potential free contact with 2 Nos. NONC.. Make Honeywell/System sensor
| a) 80 mm nominal dia | Nos | RO
| b) 100 mm nominal dia | Nos | 2
123.7 | Supply installing, testing & commissioning of inspectors test & drain assembly complete with test valve, sight glass sectional drain valve, union; necessary piping, threading, jointing & with corrosion resistant orifice all complete strictly as per drawing. Make Tyco/HD Fire/Newage
| a) 50mm | set | 2
Total Part (C)
D | EXTERNAL HYDRANT SYSTEM
124.1 | under Ground Piping - Supply installing, testing & commissioning of heavy grade GI pipes confirming to IS: 1239 Part - 1 with maleable specials confirming to IS 1239 P1 and II such as tees, elbows, checknuts, unions flanges, nipples, etc. including cutting welding fixing in/on walls, celling by using as per drawing. The quoted rate shall include PCC support blocks of suitable size etc. Fittings upto 50 mm Threaded Joint, above shall be Butt welded type. The rate quoted should e included with anticorrosive treatment with 4 mm thick polymer corrosion resistant tape as per IS 10221, overlap shall be 15mm minimum. Make:Jindal Hissar/Tata
| a) 80 mm nominal dia | Rmt | RO
| b) 100 mm nominal dia | Rmt | 24
| c) 150 mm nominal dia | Rmt | 24
124.2 | Supply installing, testing & commissioning of CI butterfly valve (PN 16) slim seal standerd lever operated type confirming to IS 13039 with required flanges, nuts, bolts etc complete.Make Audco/Intervalve/Kartar
| a) 100 mm nominal dia | Nos | 1
| b) 150 mm nominal dia | Nos | 1
124.3 | Supply, installing, testing and commissioning of Single headed oblique hydrant valve as per IS: 5290 type-A, made of SS with 63mm dia instantaneous out lets & 80mm dia flanged inlet, blank PVC cap, chain & hand wheels etc complete as required.. Make :Newage/Kartar/Safeguard | Nos | 4
124.4 | Supply, installing, testing and commissioning of 1 No of 63 mm SS branch pipe with hexagonal detachable 16 mm SS nozzle confirming IS:903, suitable for instantaneous connection to interconnect hose pipe couplings as required. Make :Newage/Kartar/Safeguard | Nos | 4
124.5 | Supply installing, testing & commissioning of Hose boxes of size 750 x 600 x 250 made of FRP (Fibre reinforced plastic) with glass fronted door, painted red outside and white inside with support/ stand to hydrant with additional supports. | Nos | 4
124.6 | Supply and fixing of 63 mm dia RRL hose tested to a bursting pressure of 32 Kg / sq.cm made of superior quality cotton and nylon jacket beaming seamless woven and rot proofed each of length 15 mtrs x 2nos. Complete with heavy quality SS coupling Make :Newage/Kartar/Safeguard | set | 4
124.7 | Supply, installation, testing & commissioning of 2 way fire brigade(IS :904) inlet connection with 63mm dia built-in SS non-return valves instantaneous coupling type with necessary acceessories . Quoted rate shall be suitable size with mounting supports etc. complete. Make :Newage/Kartar/Safeguard | Nos | 1
124.8 | Exacavation of trenches up to 1.5 mts. in depth, for laying pipes upto 150mm dia. Including forming bottom surface to required level, refilling the trenches with selected excavated earth around the pipe in layers of 150mm thick, watering, consolidating. Quoted price inclusive of disposing off / Carting away the surplus earth within the site to a dump yard as directed by the site engineer with a lead of 300 mts. etc. complete.
| a) Excavation in all kinds of soil | Cum | 30
| b) Cutting of Rock with chiselling | Cum | RO
124.9 | Construction of valve chamber with 230 mm best quality TM bricks(50kg/sqcm) in CM 1:4 over a bed of 100 mm thick PCC1:4:8, internal walls plastered smooth with necessary water proof compound in CM 1:3 and external walls plastered rough with sponge finish including curing with all necessary leads and lift and providing Medium duty FRP cover with frame (10 ton of make Aagam/ Everlast/HP) of size 900 x900 mm. Etc., Including Top slab of 300mm etc Complete.
| a) Size 1.2m x 0.9m upto depth of 1.2m (clear dimension) | Nos | 1
Total Part (D)
E | EXTINGUISHERS
125.1 | ABC FIRE EXTINGUISHER 2Kg : Supply and install in position approved make ABC Stored pressure type Fire Extinguisher 2 Kgs Capacity Mono Ammonium Phosphate based Dry Chemical Powder as per IS 14609 with ISI Mark for Fighting ABC Class of Fire, stored Pressure type of Mild steel body pressurized by Nitrogen Gas. The Extinguisher shall have pressure gauge for indicating inside pressure with opening and closing lever of squeeze grip type with tamper proof seal, complete with wall bracket. The Extinguisher is manufactured strictly as per IS: 15683:2006 with ISI mark | Nos | 8
125.2 | ABC FIRE EXTINGUISHER 6Kg : Supply and install in position approved make ABC Stored pressure type Fire Extinguisher 6 Kgs Capacity Mono Ammonium Phosphate based Dry Chemical Powder as per IS 14609 with ISI Mark for Fighting ABC Class of Fire, stored Pressure type of Mild steel body pressurized by Nitrogen Gas. The Extinguisher shall have pressure gauge for indicating inside pressure with opening and closing lever of squeeze grip type with tamper proof seal, complete with wall bracket. The Extinguisher is manufactured strictly as per IS: 15683:2006 with ISI mark. | Nos | 8
125.3 | CO2 FIRE EXTINGUISHER 4.5Kg : Supply and install in position approved make Co2 type Fire Extinguisher 4.5 Kgs Capacity, made from brand new seamless cylinder, as per IS: 7285 and CCE approval, fitted with 1 metre length Wire Braided Discharge hose and horn and Wheel type (ISI Approved) valve with wall bracket and with initial Charge as per IS: 15683-2006specification, bearing ISI Mark. | Nos | 6
125.4 | CO2 FIRE EXTINGUISHER 2Kg : Supply and install in position approved make Co2 type Fire Extinguisher 2.0 Kgs Capacity, made from brand new seamless cylinder, as per IS: 7285 and CCE approval, fitted with 1 metre length Wire Braided Discharge hose and horn and Wheel type (ISI Approved) valve with wall bracket and with initial Charge as per IS: 15683. | Nos | 1
125.5 | WATER MIST FIRE EXTINGUISHER 9.0 Ltr : Supply, Installation & Commissioining of 9Lts. Water mist type fire extinguisher, with initial filling in brand new seamless cylinder with powder coated finish, fitted with Gun Metel, stored pressure type, EPDM flexible discharge hose pipe, Squeeze grip type open/close lever, Limit proof seal, wall mounting bracket etc. complete, confirming to latest IS:15683 code. | Nos | RO
125.6 | FIRE BUCKET : Supplying of Fire Bucket of 24 guage, galvanized steel sheet, standard 9Lts capacity and of round bottom shape, painted white inside and red outside and black on the bottom dome with letters 'FIRE' in black and gold with wall mounting bracket and screws. The rate shall include the cost of river sand. Each set shall have 2Nos. | Set | RO
125.7 | FIRE BUCKET STAND : Fire bucket stand fabricated by MS angles to install 2 Nos. of buckets. | Nos | RO
Total Part (E)
TOTAL of fire protection works (Cafeteria) VIIB (A to E)
GRAND TOTAL fire protection works VII (VIIA+VIIB)
TOTAL Cost of works (I to VII)
Add GST @18%
Add BOCW @ 1%
GRAND TOTAL
NAME OF WORK: NEW HOSTEL TOWER
LOCATION: B.I.T., Mesra, Ranchi
SUMMARY
Sl. No. | Description |  |  |  | Amount
I | Civil works
(i) | Masonary works
(ii) | Plastering works
(iii) | Miscllaneous works
TOTAL OF CIVIL WORKS (I)
II | STRUCTURE WORKS
(i) | Excavation & Filling
(ii) | PCC
(iii) | RCC
(iv) | Form work/ Shuttering
(v) | Reinforcement
(vi) | Waterproofing
TOTAL FOR STRUCTURE WORKS (II)
III | ELECTRICAL WORKS
IIIA. | Hostels
(A) | Internal Cable works
(B) | Final distribution board
(C ) | UPS & Associated works
(D) | Internal wiring
( E) | Lift wiring system
(F) | Rising Main
(G) | Earthing System
(H) | Miscllaneous
(I) | LT Panel Installation
(J) | Light Fixture installation
TOTAL Electrical works (Hostel)
IIIB. | Kitchen & Cafeteria
(A) | Internal Cable works
(B) | Distribution board
(C ) | Internal wiring
(D) | Supply and Installation of Light Fitting
( E) | Lift wiring system
(F) | Earthing System
(G) | Miscllaneous
(H) | Lightening Protection system
(I) | LT Panel Installation
TOTAL Electrical works (Kitchen & Cafeteria)
IIIC. | Typical Room Electrical layout
(A) | Internal wiring
(B) | Switch & Socket
(C ) | Light Fixtures
TOTAL Electrical Rooms
IIID. | LIGHTNING PROTECTION WORKS
(A) | Ring earthing system under soil
(B) | Structural down cocductor- Riser inside column
(C ) | Terrace External Lightning Protection System
TOTAL LPS
TOTAL OF ELECTRICAL WORKS III (A to D)
IV | PHE WORKS
IVA. | PHE Works (Hostel)
(A) | Sanitary Fixtures
(B) | Water Supply System
(C ) | Drainage System
(D) | Rain water system
( E) | Hot Water System
(F) | RO Plant
TOTAL PHE Works (Hostel) IVA
IVB. | PHE Works (Cafeteria)
(A) | Sanitary Fixtures
(B) | Water Supply System
(C ) | Drainage System
(D) | Rain water system
( E) | Hot Water System
(F) | RO Plant
TOTAL PHE Works (Cafeteria) IVB
TOTAL PHE WORKS IV (IVA+IVB)
V | FAPA WORKS
VA | FAPA Works (Hostel)
(A) | Fire Alarm System
(B) | Public Address System
(C ) | Talk Back System
TOTAL FAPA System (Hostel (VA)
VB | FAPA Works (Cafeteria)
(A) | Fire Alarm System
(B) | Public Address System
(C ) | Talk Back System
TOTAL FAPA System (Hostel (VA)
TOTAL FAPA System V (VA+VB)
VI | Networking & Camera Cabling
VIA | Networking & Camera Cabling (Hostels)
VIB | Networking & Camera Cabling (Cafateria)
TOTAL Networking & Camera Cabling VI
VII | Fire protection works
VIIA | Fire protection works (Hostels)
(A) | Terrace pumps & Accessories
(B) | Internal Hydrant System
(C ) | Internal Sprinkler system
(D) | External Hydrant system
( E) | Extinguishers
TOTAL Fire protection works (Hostels) VIIA
VIIB | Fire protection works (Cafeteria)
(A) | Terrace pumps & Accessories
(B) | Internal Hydrant System
(C ) | Internal Sprinkler system
(D) | External Hydrant system
( E) | Extinguishers
TOTAL Fire protection works (Hostels) VIIA
TOTAL of Fire protection works VII (VIIA+VIIB)
TOTAL (I to VII)
Add GST @18%
Add BOCW @ 1%
GRAND TOTAL
NAME OF WORK: NEW HOSTEL TOWER
LOCATION: B.I.T., Mesra, Ranchi
SUMMARY
Sl. No. | Description
I | STRUCTURE WORKS
(i) | Excavation & Filling
(ii) | PCC
(iii) | RCC
(iv) | Form work/ Shuttering
(v) | Reinforcement
(vi) | Waterproofing
TOTAL FOR STRUCTURE WORKS (I)
II | Civil works
(i) | Masonary works
(ii) | Plastering works
(iii) | Miscllaneous works
TOTAL OF CIVIL WORKS (II)
III | ELECTRICAL WORKS
IIIA. | Hostels
(A) | Internal Cable works
(B) | Final distribution board
(C ) | UPS & Associated works
(D) | Internal wiring
( E) | Lift wiring system
(F) | Rising Main
(G) | Earthing System
(H) | Miscllaneous
(I) | LT Panel Installation
(J) | Light Fixture installation
TOTAL Electrical works (Hostel)
IIIB. | Kitchen & Cafeteria
(A) | Internal Cable works
(B) | Distribution board
(C ) | Internal wiring
(D) | Supply and Installation of Light Fitting
( E) | Lift wiring system
(F) | Earthing System
(G) | Miscllaneous
(H) | Lightening Protection system
(I) | LT Panel Installation
TOTAL Electrical works (Kitchen & Cafeteria)
IIIC. | Typical Room Electrical layout
(A) | Internal wiring
(B) | Switch & Socket
(C ) | Light Fixtures
TOTAL Electrical Rooms
IIID. | LIGHTNING PROTECTION WORKS
(A) | Ring earthing system under soil
(B) | Structural down cocductor- Riser inside column
(C ) | Terrace External Lightning Protection System
TOTAL LPS
TOTAL OF ELECTRICAL WORKS III (A to D)
IV | PHE WORKS
IVA. | PHE Works (Hostel)
(A) | Sanitary Fixtures
(B) | Water Supply System
(C ) | Drainage System
(D) | Rain water system
( E) | Hot Water System
(F) | RO Plant
TOTAL PHE Works (Hostel) IVA
IVB. | PHE Works (Cafeteria)
(A) | Sanitary Fixtures
(B) | Water Supply System
(C ) | Drainage System
(D) | Rain water system
( E) | Hot Water System
(F) | RO Plant
TOTAL PHE Works (Cafeteria) IVB
TOTAL PHE WORKS IV (IVA+IVB)
V | FAPA WORKS
VA | FAPA Works (Hostel)
(A) | Fire Alarm System
(B) | Public Address System
(C ) | Talk Back System
TOTAL FAPA System (Hostel (VA)
VB | FAPA Works (Cafeteria)
(A) | Fire Alarm System
(B) | Public Address System
(C ) | Talk Back System
TOTAL FAPA System (Hostel (VA)
TOTAL FAPA System V (VA+VB)
VI | Networking & Camera Cabling
VIA | Networking & Camera Cabling (Hostels)
VIB | Networking & Camera Cabling (Cafateria)
TOTAL Networking & Camera Cabling VI
VII | Fire protection works
VIIA | Fire protection works (Hostels)
(A) | Terrace pumps & Accessories
(B) | Internal Hydrant System
(C ) | Internal Sprinkler system
(D) | External Hydrant system
( E) | Extinguishers
TOTAL Fire protection works (Hostels) VIIA
VIIB | Fire protection works (Cafeteria)
(A) | Terrace pumps & Accessories
(B) | Internal Hydrant System
(C ) | Internal Sprinkler system
(D) | External Hydrant system
( E) | Extinguishers
TOTAL Fire protection works (Hostels) VIIA
TOTAL of Fire protection works VII (VIIA+VIIB)
TOTAL (I to VII)
Add GST @18%
Add BOCW @ 1%
GRAND TOTAL